## Report_DPS (HPSLDC)
| File Name: DAILY POWER SUPPLY- | 2021-07-09
Hiamchal Pradesh State Load Despatch Centre
Government of Himahcal Pradesh
|  | E-Mail sehpsldc@gmail.com |  |  |  |  | Dated | 2021-07-10
FROM: |  |  |  | TO
| POWER CONTROLLER |  |  |  | Managing Director
| HPSLDC, GoHP, Totu, Shimla-11 |  |  |  | HP State Load Despatch Centre
| (FAX #: 0177 2837543) |  |  |  | Govt. of HP, Totu, Shimla-11
Eamail:mdhpsldc@gmail.com
Subject:- Daily Power Supply Position For Dated |  |  | 2021-07-09
Sir,
The daily Power Supply Position is tabulated as under :-
S.No. | POWER HOUSES UNDER HPSEBL | INSTALLED CAPACITY (MW) | DAILY GENERATION TARGET ON YEARLY BASIS [CE (Gen)/IPP] Lakh Units | DAILY GENERATION TARGET ON WEEKLY BASIS (SLDC) LU on Previous year Trend | ESTIMATED GENERATION ON DAYAHEAD BASIS FROM HPSEBL P/ H's / IPP) Lakh Units | ACTUAL (Lakh Units) | MAX Gen. Mega Watts | REMARKS | [7 empty] | 34.25
( Reason for Major Variation)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | LARJI (3x42 MW) | 126 | 23.19 | 23.19 | 28.32 | 29.34 | 125
2 | BHABA (3x40 MW) | 120 | 19.2 | 19.2 | 31.2 | 31.36 | 131
3 | BASSI (4x16.50MW) | 66 | 9.8 | 9.8 | 15.84 | 14.65 | 66
4 | GIRI (2x30 MW) | 60 | 0.73 | 0.73 | 3.23 | 2.71 | 30
5 | GANVI-I(2x11.25 MW) | 22.5 | 4.07 | 4.07 | 1.92 | 5.28 | 22.8
6 | ANDHRA (3x5.65 MW) | 16.95 | 1.71 | 1.71 | 1.72 | 2.21 | 12
7 | BANER (3x4 MW) | 12 | 0.87 | 0.87 | 1.68 | 1.5 | 8
8 | KHAULI (2x6 MW) | 12 | 0.81 | 0.81 | 2.88 | 2.26 | 11
9 | GAJ ( 3x3.5 MW) | 10.5 | 0.92 | 0.92 | 1.2 | 2.02 | 9.7
10 | GANVI-II(2x5) | 10 | 2.41 | 2.41 | 1.2 | 2.35 | 10.05
11 | BINWA (2x3 MW) | 6 | 0.73 | 0.73 | 1.44 | 0.68 | 3
12 | THIROT (3x1.5 MW) | 4.5 | 0.25 | 0.25 | 0.36 | 0.36 | 2.2 |  | Anticipated/ Estimated Generation |  |  | 165.022
13 | MINI/MICRO ** (30.95 MW) | 30.95 | 1.53 | 1.52 | 1.61 | 1.73
A | TOTAL HPSEBL Gen.(1 to 12) | 497.4 | 66.22 | 66.21 | 92.6 | 96.45 |  |  | Total actual Gen. |  |  | 224.7606
B | IPP's Generation |  |  |  |  | Actual Availed by HPSEBL |  | Total Generation of Baspa-II in LUs
i) | Baspa (3 X100MW) IPP
| (a) 88% | 300 | 10.56 | 8.2896 | 69.696 | 69.2912 | 330 | 78.74
| (b) 12% |  | 1.44 | 1.1304 | 9.504 | 9.4488 |  | Total Generation of Malana
ii) | Malana (2X43 MW) IPP HP Share (20%) | 86 | 0.446 | 0.646 | 4.332 | 4.372 | 92 | 21.86
Total Generation of IPP's selling out side in Lus
64.1036
iii) | KASHANG (3x65 MW) | 195 | 0 | 0 | 13.77 | 13.1606 | 71
iiia) | SAWRA KUDDU (37x3) | 111 |  | 0 | 10.83 | 10.8862 | 74
iv) | MICRO i/c Patikari & Toss (IPP) | 77 |  |  | 51.6 | 58.23
v) | IPP's Power (Phojal, Baner Sangam, Chanju, Suryaakanta, Sandhya, Kashang, Nanti, Bharagarh & Goodwill ) | - | - | - | 7.052 | 4.6813 | 55 | 56.92 |  |  | ='Form-1_AnticipatedVsActual_BI'!V19+'Form-1_AnticipatedVsActual_BI'!V24+'Form-1_AnticipatedVsActual_BI'!V30+'Form-1_AnticipatedVsActual_BI'!V36+'Form-1_AnticipatedVsActual_BI'!V42+'Form-1_AnticipatedVsActual_BI'!V49+'Form-1_AnticipatedVsActual_BI'!V55
| Summary:- | [6 empty] | All Figures in LU's |  |  | -10
1 | HPSEBL Generation |  | 96.45 | 21 | EXPORT THROUGH BANKING/SALE |  | At NR Periphery | At HP Periphery |  |  | 36.95
2 | Baspa-II |  | 78.74 |  | HPSEBL Export through IEX+ PXIL | (A)Market Sale through IEX | 0 | 0
3 | Solar IPP's |  | 0.81381 |  |  | (B) Sale through RTM | 3.825 | 3.825
4 | MICRO (IPP ) |  | 58.23 |  |  | IEX DAM Rate Rs. 4.59 & TAM Rate /kwh
5 | SINGRAULI_SOLAR |  | 0.35088 |  |  | (C ) Total (A+B) |  | 3.825
6 | SECI-Solar (LTA PURCHASE) |  | 1.1667 |  |  |  | 0 | 0
7 | Total Central Sector including SOR & GoHP Share in NJPC, B'suil, CH-I, CH-II (HP Periphery) |  | 349.448
8 | Free Power to HPSEBL from IPPs (Selling under OA) : Malana, Phojal, Baner Sangam, Chanju HEP, Kashang, Suryakanta, Nanti, Sandhaya, Bharagarh & Goodwill(KUT) |  | 9.0533
9 | Bilateral Share (Shanan+RSD+UP+UK) |  | 22.5456 | [5 empty] | x2
10 | Total availability (1 to 4 + 6 to 9) |  | 616.4474 |  | AS & WHEN BANKING
11 | Total GoHP Power as per last revision. |  | 287.901 |  |  |  | 0 | 0 | [8 empty] | 138.0664
12 | Actual GoHP share sold out side HP to other states FP 12% in Ch-1, Ch-2, B.Suil, FP 13% in Ch3, Parbati-3, 13 % FP in Rampur, FP 12% NJPC & Koldam purchased form GoHP @ Rs.2.66 |  | 124.8112 |  | IPCL & MePDCL through APPCPL (As & When Banking) |  | 0 | 0
13 | GoHP share Schedule to HPSEBL Equity : NJPC 22%, Rampur 26.1%, Koldam 15% UA & SOR |  | 157.6429 |  | FIRM BANKING :-
14 | Additional RTM/URS power Purchased GoHP |  | 0 |  | BRPL THROUGH M/s MPL (AP-88024) |  | 43.2 | 43.2
15 | GoHP Power in/out (+/-) from the Grid |  | 5.4468 |  |  |  | 0 | 0
16 | SOR |  | 17.9206 |  | RE POWER :-
17 | Malana & other IPP's (selling out side) in/out (+/-) from HPSEBL system |  | -6.5021 |  | PSPCL (RE Through M/s PTC) |  | 16.8 | 16.8 | 17 | =((Report_DPS!$I$35*0.8)*0.96)-ABS('Form-1_AnticipatedVsActual_BI'!$L$28)+(('Form-1_AnticipatedVsActual_BI'!$G31*1)*0.9525)-ABS('Form-1_AnticipatedVsActual_BI'!$L31)+(('Form-1_AnticipatedVsActual_BI'!$G32*0.87)*0.96)-ABS('Form-1_AnticipatedVsActual_BI'!$L32)
18 | Net Availability with HPSEBL (10-12+17) |  | 485.134 |  | GOA (Through APPCL) |  | 6.2064 | 6.2064
19 | IMPORT THROUGH BANKING/ PURCHASE | At NR Periphery | At HP Periphery |  | GOA (Through MPL) |  | 6.12 | 6.12
| Market Purchase (OA Consumers) | 0 | 0 |  | TPDDL DELHI (RE Through M/s TPTCL) Night Power |  | 79.44 | 79.44 | 29.3904
| HPSEBL Import Through IEX @ 3.45 | 9.3625 | 9.0835 |  | ODHISA & DIAPL (GMRETL) |  | 13.5 | 13.5
| Import through RTM IEX | 3.1642 | 3.0699 |  | PSPCL (RE Through M/s PTC) Night Power |  | 16 | 16
| 0 | 0 | 0 |  |  |  | 0 | 0
| 0 | 0 | 0 |  |  |  | 0 | 0 | OD/UD During Min./Max. Frequency
| 0 | 0 | 0 | 22 | Total Export |  | 185.0914 | 185.0914 | Min. Freq. | Time | O/D | U/D | Max. Freq. | Time | O/D | U/D | Average .Freq.
| 0 | 0 | 0 | 23 | Availability after Import/Export (18+20-22) |  |  | 312.196 | 49.85 | 06.00 | 0 | 6.66 | 50.12 | 10.00 | 8.18 | 0 | 50.0106
| 0 | 0 | 0 | 24 | Demand of the State |  |  | 315.393
|  | 0 | 0 | 25 | Over/Under drawl(-/+) [23-24] |  |  | -3.197
|  | 0 | 0 | 26 | Tentative UI rate in Rupees (OD & UD), Avg |  |  | 2.27 , 1.81 & 2.79 |  |  |  | G67 | ="Gas:" & IF('Surrendered Energy'!AX105<0,0,ROUND('Surrendered Energy'!AX105,2))&" & Thermal:" &IF('Surrendered Energy'!AY105<0,0,ROUND('Surrendered Energy'!AY105,2))
|  | 0 | 0 | 27 | Load Shedding |  |  | 4.0333 |  |  |  | I67 | =IF(AND('Surrendered Energy'!AY105<0,'Surrendered Energy'!AX105<0),0,IF(AND('Surrendered Energy'!AY105>=0,'Surrendered Energy'!AX105>=0),('Surrendered Energy'!AY105+'Surrendered Energy'!AX105),IF('Surrendered Energy'!AX105>0,'Surrendered Energy'!AX105,'Surrendered Energy'!AY105)))
|  | 0 | 0 | 28 | Unrestricted Demand |  |  | 319.4263
|  |  |  | 29 | Average Frequency (Hz) :(Max.Freq. 50.12 at 10.00 Hrs, Min.Freq. 49.85 at 06.00 Hrs) |  |  | 50.0106
|  |  |  | 30 | Max Demand observed (MW) (at 10.00 Hrs.) |  |  | 1489.5
|  |  |  | 31 | Min Demand at observed (MW) (at 04.45 Hrs.) |  |  | 1097.66
|  |  |  | 32 | Central Share Surrendered | LF & RF |  | 13.731
[6 empty] | Gas: 0 & Thermal: 0.81 |  | 0.80879
20 | Total Import by HPSEBL | 12.5267 | 12.1534 |  |  | Total Surrendered :(Amount: 94.1 Lacs, Avg. Rate: 8.85) |  | 14.5398
21 | URS Booked |  | 0.60367 |  | INDUSTRIAL CONSUMPTION |  |  | 217.2184
22 | Availability with HP (18-21) |  | 484.5303
* Means no communication. Generation assumed.
** Includes Generation of mini/micro power Houses of HPSEBL.
Copy to:-
| The Chief Engineer (HPSLDC), GoHP, Totu, Shimla-11. | [5 empty] | Shift Incharge
HPSLDC, GoHP, Totu,Shimla-11.
1 | Own | 234.2338
2 | Central Sector | 349.448
3 | Bilateral (Shared+Malana afterExport) | 22.5456
4 | GoHP Power (in/out) | 124.8112
5 | Malana (in/out) | -6.5021
. | OD/UD |  | -3.197
| Total Gen. | Demand Met | Max Demand Met MW | RE/Green Power Sold (Lus)
| 234.2338 | 315.393 | 1489.5 | 60
Note on D61: ControlRoom:
Note on D63: Malana, Phojal, Baner Sangam, Chanju HEP, Kashang, Suryakanta, Nanti, Sandhaya, Bharagarh & Goodwill(KUT) (in/out)
Note on I74: dba: