## Report_DPS (HPSLDC)
| File Name: DAILY POWER SUPPLY- | 2021-07-22
Hiamchal Pradesh State Load Despatch Centre
Government of Himahcal Pradesh
|  | E-Mail sehpsldc@gmail.com |  |  |  |  | Dated | 2021-07-23
FROM: |  |  |  | TO
| POWER CONTROLLER |  |  |  | Managing Director
| HPSLDC, GoHP, Totu, Shimla-11 |  |  |  | HP State Load Despatch Centre
| (FAX #: 0177 2837543) |  |  |  | Govt. of HP, Totu, Shimla-11
Eamail:mdhpsldc@gmail.com
Subject:- Daily Power Supply Position For Dated |  |  | 2021-07-22
Sir,
The daily Power Supply Position is tabulated as under :-
S.No. | POWER HOUSES UNDER HPSEBL | INSTALLED CAPACITY (MW) | DAILY GENERATION TARGET ON YEARLY BASIS [CE (Gen)/IPP] Lakh Units | DAILY GENERATION TARGET ON WEEKLY BASIS (SLDC) LU on Previous year Trend | ESTIMATED GENERATION ON DAYAHEAD BASIS FROM HPSEBL P/ H's / IPP) Lakh Units | ACTUAL (Lakh Units) | MAX Gen. Mega Watts | REMARKS | [7 empty] | 36.81
( Reason for Major Variation)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | LARJI (3x42 MW) | 126 | 23.19 | 23.19 | 28.8 | 28.62 | 120
2 | BHABA (3x40 MW) | 120 | 19.2 | 19.2 | 31.2 | 30.33 | 131
3 | BASSI (4x16.50MW) | 66 | 9.8 | 9.8 | 15.84 | 13.89 | 66
4 | GIRI (2x30 MW) | 60 | 0.73 | 0.73 | 7.2 | 14.22 | 60
5 | GANVI-I(2x11.25 MW) | 22.5 | 4.07 | 4.07 | 1.92 | 5.41 | 22.9
6 | ANDHRA (3x5.65 MW) | 16.95 | 1.71 | 1.71 | 1.72 | 3.01 | 16.95
7 | BANER (3x4 MW) | 12 | 0.87 | 0.87 | 1.68 | 2.57 | 12
8 | KHAULI (2x6 MW) | 12 | 0.81 | 0.81 | 2.88 | 2.96 | 22.9
9 | GAJ ( 3x3.5 MW) | 10.5 | 0.92 | 0.92 | 1.2 | 0.94 | 8.6
10 | GANVI-II(2x5) | 10 | 2.41 | 2.41 | 1.2 | 1.99 | 10.06
11 | BINWA (2x3 MW) | 6 | 0.73 | 0.73 | 1.44 | 1.36 | 6.2
12 | THIROT (3x1.5 MW) | 4.5 | 0.25 | 0.25 | 0.45 | 0.33 | 2.2 |  | Anticipated/ Estimated Generation |  |  | 187.6325
13 | MINI/MICRO ** (30.95 MW) | 30.95 | 1.53 | 1.52 | 1.91 | 1.91
A | TOTAL HPSEBL Gen.(1 to 12) | 497.4 | 66.22 | 66.21 | 97.44 | 107.54 |  |  | Total actual Gen. |  |  | 257.4309
B | IPP's Generation |  |  |  |  | Actual Availed by HPSEBL |  | Total Generation of Baspa-II in LUs
i) | Baspa (3 X100MW) IPP
| (a) 88% | 300 | 10.56 | 8.2896 | 69.696 | 69.8104 | 330 | 79.33
| (b) 12% |  | 1.44 | 1.1304 | 9.504 | 9.5196 |  | Total Generation of Malana
ii) | Malana (2X43 MW) IPP HP Share (20%) | 86 | 0.446 | 0.646 | 4.538 | 4.904 | 103.6 | 24.52
Total Generation of IPP's selling out side in Lus
69.5876
iii) | KASHANG (3x65 MW) | 195 | 0 | 0 | 14.26 | 15.8602 | 71.5
iiia) | SAWRA KUDDU (37x3) | 111 |  | 0 | 10.28 | 11.8008 | 74
iv) | MICRO i/c Patikari & Toss (IPP) | 77 |  |  | 68.34 | 74.82
v) | IPP's Power (Phojal, Baner Sangam, Chanju, Suryaakanta, Sandhya, Kashang, Nanti, Bharagarh & Goodwill ) | - | - | - | 7.5925 | 5.1635 | 55 | 59.2107 |  |  | ='Form-1_AnticipatedVsActual_BI'!V19+'Form-1_AnticipatedVsActual_BI'!V24+'Form-1_AnticipatedVsActual_BI'!V30+'Form-1_AnticipatedVsActual_BI'!V36+'Form-1_AnticipatedVsActual_BI'!V42+'Form-1_AnticipatedVsActual_BI'!V49+'Form-1_AnticipatedVsActual_BI'!V55
| Summary:- | [6 empty] | All Figures in LU's |  |  | -10
1 | HPSEBL Generation |  | 107.54 | 21 | EXPORT THROUGH BANKING/SALE |  | At NR Periphery | At HP Periphery |  |  | 36.95
2 | Baspa-II |  | 79.33 |  | HPSEBL Export through IEX+ PXIL | (A)Market Sale through IEX | 9.2578 | 9.2578
3 | Solar IPP's |  | 0.43335 |  |  | (B) Sale through RTM | 6.8 | 6.8
4 | MICRO (IPP ) |  | 74.82 |  |  | IEX DAM Rate Rs. 2.75 & TAM Rate /kwh
5 | SINGRAULI_SOLAR |  | 0.44675 |  |  | (C ) Total (A+B) |  | 16.0578
6 | SECI-Solar (LTA PURCHASE) |  | 1.2694 |  |  |  | 0 | 0
7 | Total Central Sector including SOR & GoHP Share in NJPC, B'suil, CH-I, CH-II (HP Periphery) |  | 332.7237
8 | Free Power to HPSEBL from IPPs (Selling under OA) : Malana, Phojal, Baner Sangam, Chanju HEP, Kashang, Suryakanta, Nanti, Sandhaya, Bharagarh & Goodwill(KUT) |  | 10.0675
9 | Bilateral Share (Shanan+RSD+UP+UK) |  | 22.93 | [5 empty] | x2
10 | Total availability (1 to 4 + 6 to 9) |  | 629.1139 |  | AS & WHEN BANKING
11 | Total GoHP Power as per last revision. |  | 293.1938 |  |  |  | 0 | 0 | [8 empty] | 139.0264
12 | Actual GoHP share sold out side HP to other states FP 12% in Ch-1, Ch-2, B.Suil, FP 13% in Ch3, Parbati-3, 13 % FP in Rampur, FP 12% NJPC & Koldam purchased form GoHP @ Rs.3.08 |  | 126.452 |  | IPCL & MePDCL through APPCPL (As & When Banking) |  | 0 | 0
13 | GoHP share Schedule to HPSEBL Equity : NJPC 22%, Rampur 26.1%, Koldam 15% UA & SOR |  | 157.935 |  | FIRM BANKING :-
14 | Additional RTM/URS power Purchased GoHP |  | 0 |  | BRPL THROUGH M/s MPL (AP-88024) |  | 48 | 48
15 | GoHP Power in/out (+/-) from the Grid |  | 8.8068 |  |  |  | 0 | 0
16 | SOR |  | 18.3084 |  | RE POWER :-
17 | Malana & other IPP's (selling out side) in/out (+/-) from HPSEBL system |  | -4.2311 |  | PSPCL (RE Through M/s PTC) |  | 15.6 | 15.6 | 17 | =((Report_DPS!$I$35*0.8)*0.96)-ABS('Form-1_AnticipatedVsActual_BI'!$L$28)+(('Form-1_AnticipatedVsActual_BI'!$G31*1)*0.9525)-ABS('Form-1_AnticipatedVsActual_BI'!$L31)+(('Form-1_AnticipatedVsActual_BI'!$G32*0.87)*0.96)-ABS('Form-1_AnticipatedVsActual_BI'!$L32)
18 | Net Availability with HPSEBL (10-12+17) |  | 507.2376 |  | GOA (Through APPCL) |  | 6.2064 | 6.2064
19 | IMPORT THROUGH BANKING/ PURCHASE | At NR Periphery | At HP Periphery |  | GOA (Through MPL) |  | 6.12 | 6.12
| Market Purchase (OA Consumers) | 11.6679 | 11.312 |  | TPDDL DELHI (RE Through M/s TPTCL) Night Power |  | 81.6 | 81.6 | 47.3832
| HPSEBL Import Through IEX @ 0 | 0 | 0 |  | ODHISA & DIAPL (GMRETL) |  | 13.5 | 13.5
| Import through RTM IEX | 0.37506 | 0.36362 |  | PSPCL (RE Through M/s PTC) Night Power |  | 16 | 16
| 0 | 0 | 0 |  |  |  | 0 | 0
| 0 | 0 | 0 |  |  |  | 0 | 0 | OD/UD During Min./Max. Frequency
| 0 | 0 | 0 | 22 | Total Export |  | 203.0842 | 203.0842 | Min. Freq. | Time | O/D | U/D | Max. Freq. | Time | O/D | U/D | Average .Freq.
| 0 | 0 | 0 | 23 | Availability after Import/Export (18+20-22) |  |  | 315.829 | 49.93 | 21.30 | 63.26 | 0 | 50.09 | 13.30 | 0 | 29.28 | 50.0128
| 0 | 0 | 0 | 24 | Demand of the State |  |  | 310.605
|  | 0 | 0 | 25 | Over/Under drawl(-/+) [23-24] |  |  | 5.224
|  | 0 | 0 | 26 | Tentative UI rate in Rupees (OD & UD), Avg |  |  | 2.57 , 0.61 & -0.66 |  |  |  | G67 | ="Gas:" & IF('Surrendered Energy'!AX105<0,0,ROUND('Surrendered Energy'!AX105,2))&" & Thermal:" &IF('Surrendered Energy'!AY105<0,0,ROUND('Surrendered Energy'!AY105,2))
|  | 0 | 0 | 27 | Load Shedding |  |  | 0 |  |  |  | I67 | =IF(AND('Surrendered Energy'!AY105<0,'Surrendered Energy'!AX105<0),0,IF(AND('Surrendered Energy'!AY105>=0,'Surrendered Energy'!AX105>=0),('Surrendered Energy'!AY105+'Surrendered Energy'!AX105),IF('Surrendered Energy'!AX105>0,'Surrendered Energy'!AX105,'Surrendered Energy'!AY105)))
|  | 0 | 0 | 28 | Unrestricted Demand |  |  | 310.605
|  |  |  | 29 | Average Frequency (Hz) :(Max.Freq. 50.09 at 13.30 Hrs, Min.Freq. 49.93 at 21.30 Hrs) |  |  | 50.0128
|  |  |  | 30 | Max Demand observed (MW) (at 10.45 Hrs.) |  |  | 1480.78
|  |  |  | 31 | Min Demand at observed (MW) (at 03.45 Hrs.) |  |  | 1071.44
|  |  |  | 32 | Central Share Surrendered | LF & RF |  | 14.1151
[6 empty] | Gas: 0 & Thermal: 13.44 |  | 13.4351
20 | Total Import by HPSEBL | 12.0429 | 11.6756 |  |  | Total Surrendered :(Amount: 106.65 Lacs, Avg. Rate: 5.87) |  | 27.5502
21 | URS Booked |  | 0.031441 |  | INDUSTRIAL CONSUMPTION |  |  | 215.0807
22 | Availability with HP (18-21) |  | 507.2062
* Means no communication. Generation assumed.
** Includes Generation of mini/micro power Houses of HPSEBL.
Copy to:-
| The Chief Engineer (HPSLDC), GoHP, Totu, Shimla-11. | [5 empty] | Shift Incharge
HPSLDC, GoHP, Totu,Shimla-11.
1 | Own | 262.1233
2 | Central Sector | 332.7237
3 | Bilateral (Shared+Malana afterExport) | 22.93
4 | GoHP Power (in/out) | 126.452
5 | Malana (in/out) | -4.2311
. | OD/UD |  | 5.224
| Total Gen. | Demand Met | Max Demand Met MW | RE/Green Power Sold (Lus)
| 262.1233 | 310.605 | 1480.78 | 63.6
Note on D61: ControlRoom:
Note on D63: Malana, Phojal, Baner Sangam, Chanju HEP, Kashang, Suryakanta, Nanti, Sandhaya, Bharagarh & Goodwill(KUT) (in/out)
Note on I74: dba: