## Sheet1
Status of healthiness of Telemetry System installed at SLDC Control Centre, Shimla as on 13.07.2021 at 11:00 AM
Sr. No. | Description | Contact Number | Contact Person | Communication |  | Speech |  | Status of Telemetry | E-Mail | Date | Remarks
|  |  |  | Protocol | Media | No. | Status
1 | 2 | 3 | 4 | 5 | 6 |  |  | 7 | 9 | 10 | 11
A | IPP's
1 | Baspa | 9805002260, 9816805258 | Ravindera Rana (DGM), Vikas Gupta (AGM) | 101 | GPRS |  |  | ok | baspa.powerhouse@jsw.in
2* | Malana HEP | 9816099653 | Mohamed Rafiq (Manager Electrical) | 101 | PLCC/OPGW |  |  | ok | malanageneration@lnjbhilwara.com
3* | Baner Sangam SHEP (Yogindra) | 7833989965 | Mr. Suraj Kumar | 101 | GPRS |  |  | ok | suraj452003@yahoo.co.in
4 | Jogini SHEP | 9805296267 | Nagasiva Reddy (plant incharge) | 104 | GPRS |  |  | Not ok | sunitakapoorsldc@gmail.com | Not Reporting since 06.07.2021 | Analog data & Digital status is suspected
5* | Baragran HEP (Kanchunjunga) | 9560254005 | Prashun (plant incharge) | 104 | GPRS |  |  | ok | prasun@polyplex.com
6* | Chanju HEP | 7807878901 | D.R Sharma (Plant Head) | 104 | Lease Line/GPRS |  |  | ok | purchase.shimla@goelgroup.co.in
7 | Sumez SHEP | 9816123344 | Pushp Pev (Plant Head) | 104 | GPRS |  |  | ok | pushpdev.s@greenkogroup.com
8* | Nanti Pooling Station (33/66kV) | 9816955800 | Anil Rana (Plant incharge) | 104 | GPRS |  |  | ok | arana.shp08@gmail.com
9* | Balargha SHEP (Sandhya) | 9805073754 | Tushar Sharma (Shift Incharge) | 104 | GPRS |  |  | ok | deepeshkumar.roy@continuumenergy.in
10* | Manuni SHEP | 7018013078 | Sanjeev mittal (GM) | 104 | GPRS |  |  | Not ok | manunihep@redeffmail.com | Not Reporting today i.e. 13.07.2021 | Analog data & Digital status is suspected
11 | Brua SHEP | 7807312069 | Neerath Singh | 104 | GPRS |  |  | Not ok | rajcheelasingh@gmail.com | Not Reporting since 18.09.2019. | Analog data & Digital status is suspected
12 | Sarwari-III SHEP | 8894778734 | Inderjit (Plant Head) | 104 | GPRS |  |  | Not ok | inderjeetsharma73@yahoo.com | Not Reporting since 12.07.2021 | Analog data & Digital status is suspected
13 | Lower Aleo SHEP (Baragarh) |  |  | 104 | GPRS |  |  | Not ok | baragarhhydro2005@gmail.com | Not Reporting since 08.07.2021 | Analog data & Digital status is suspected
14 | Kota Gad SHEP | 9418073460 | Rajeev (Authorized Signatory) | 104 | GPRS |  |  | ok | carajeev1@gmail.com
15 | GR Enterprises Solar PP | 8894380675 | Mohan singh (J.E.) | 104 | GPRS |  |  | Not ok | mohansinghsolarplant@gmail.com | Not Reporting since 12.07.2021 | Analog data & Digital status is suspected
16 | KK Kashyap Solar PP | 9818814181 | Yashveer Singh (Plant Head) | 104 | GPRS |  |  | ok | kksolarpower@gmail.com
17 | Upper Joiner SHEP | 8894870861 | Anil (Plant Head) | 104 | GPRS |  |  | ok | somashekar.s@greenkogroup.com
18 | Lucky Brass Solar PP | 9459640219 | Sanjay Diman (Project manager) | 104 | GPRS |  |  | ok | luckybrass@rediffmail.com
19 | RP Suman | 7972744454 | RP Suman (Plant Owner) | 104 | GPRS |  |  | Not ok | amitlakhanpal77@gmail.com | Not Reporting since 07.11.2020 | Analog data & Digital status is suspected
20 | LEOND Hydro | 7018400391 | Divij (Plant Head) | 104 | GPRS |  |  | Not ok | divijsharma@jayahydro.com | Not Reporting since 12.07.2021 | Analog data & Digital status is suspected
21 | Satya Sai Hydro | 8628871917 | Anup (Plant Head) | 104 | GPRS |  |  | ok | akumaranoop32@gmail.com
22* | Kut Hydro | 8448390088 | Rahul Kumar ( Executive IT) | 104 | GPRS |  |  | Not ok | kutgoodwill@kundangroup.com | Not Reporting since 12.07.2021 | Analog data & Digital status is suspected
23 | Jeori HEP THIPL | 8278823224 | Mr. Dheeraj Kumar | 104 | GPRS |  |  | ok | dheeraj.v@greenkogroup.com
24 | Raura Hydro | 9805651955 | Vinit (Plant Head) | 104 | GPRS |  |  | Not ok | vthakur@dlz.com | Not Reporting since 23.04.2021 | Analog data & Digital status is suspected
25 | Siunr SHEP | 8894778734 | Varun (Plant Head) | 104 | GPRS |  |  | Not ok | usaka.varun.kullu@gmail.com | Not Reporting since 12.07.2021 | Analog data & Digital status is suspected
26 | Pinnacle Hydro | 9816307488 | Kaushal (Plant Head) | 104 | GPRS |  |  | ok | er.koshal@gmail.com
27 | Malana- II | 9805078444 |  | 104 | GPRS |  |  | ok | anandvarma17@everestpower.in
28 | Rala (Taranda) | 9816852194 | Gopal (Plant Head) | 104 | GPRS |  |  | ok | trandapower@gmail.com
29 | Kurmi SHEP |  |  | 104 | GPRS |  |  | ok
30 | Chaur | 9805519785 | Lalit (Site Engineer) | 101 | PLCC/OPGW |  |  | Not ok | substation@everestpower.in | Not Reporting since 02.07.2021 | Analog data & Digital status is suspected
31 | Upper Nanti |  |  | 104 | GPRS |  |  | ok
32 | Wanger Homte | 9805649114 | Mr. Lakshmi Narayana (Project Manager) | 104 | GPRS |  |  | ok | wangerhomte@gmail.com
B | HPPCL Stations
1* | Kashang HEP | 8894321440 | Rishab (Executive Engineer) | 101 | GPRS |  |  | Not ok | ikhepshiftincharge@gmail.com | Not Reporting since 12.07.2021 | Analog data & Digital status is suspected
2 | Sainj HEP | 7018334956 | Mr. Manish Chaudhari | 104 | GPRS |  |  | ok | sm.e.sainj@gmail.com
3 | Berra Dol Solar | 7018301778 | Anil Kumar (JE) | 101 | GPRS |  |  | ok | gm_elect@hppcl.in
4 | Sawra Kuddu | 9418340530 | Rajneesh Kumar | 104 | OPGW |  |  | ok | dgmelectrical.skhep@gmail.com
C | Open Access Consumers
1* | ACC Barmana, Kangoo | 9816016949 | Anshul Gupta (Plant incharge) | 104 | GPRS |  |  | Not Ok | anshul.gupta@acclimited.com | Not Reporting since 06.07.2021 | Analog data & Digital status is suspected
2* | Ambuja Cement (Rauri) | 981602351, 9805009602 | Rohit kumar, Kishori lal (AE darla) | 104 | GPRS |  |  | Ok | deepak.dhiman@ambujacement.com
3* | Ultra-Tech Cement, Bagga | 9805002920 | Mr. ID Prasad | 101 | PLCC |  |  | Not Ok | naveen.kagrawal@adityabirla.com | Not Reporting since 11.05.2021 | Analog data & Digital status is suspected
4 | Vardhman, Baddi | 8894723203 | DR Sharma (Plant Incharge) | 104 | GPRS |  |  | Ok | drsharma@vardhman.com
5* | Birla Textile, Baddi | 9318760937 | Ramesh Mishra (plant incharge) | 104 | GPRS |  |  | Ok | msarora@sutlejtextiles.com
6* | Winsome I, Baddi | 7018013078 | Sanjeev mittal (GM) | 104 | GPRS |  |  | ok | smittal@winsometextile.com
7* | Ultra-Tech Cement, Bageri | 9805375871 | N.S Rawat (AE) | 104 | GPRS |  |  | Ok | ashwani.kumar@adityabirla.com
8* | Ambuja Cement (Nalagarh) | 9418075526, 9815609789 | Devraj, Alok Sharma (DGM) | 104 | GPRS |  |  | Ok | deepak.dhiman@ambujacement.com
9* | Ambuja Cement (Sulli) | 981602351, 9805009602 | Rohit kumar, Kishori lal (AE darla) | 104 | GPRS |  |  | Ok | kishori.sharma@ambujacement.com
D | HPPTCL Stations
1 | Phojal | 9418464084 | Arun kumar (JE) | 101 | GPRS |  |  | Ok | smphojal@hpptcl.in
2 | Karian | 9805413394 | Er. Kanav (AE) | 104 | GPRS |  |  | Ok | dmkarianchamba@hpptcl.in
3 | Bhoktoo | 9816698731 | Dilip Kumar (JE) | 101 | GPRS |  |  | Ok | dmebhaba1@hpptcl.in
4 | Wangtoo | 8628829397 | Ishita (AE) | 104 | GPRS |  |  | Not ok | wangtoosubstation@hpptcl.in | Not Reporting today i.e. 13.07.2021 | Analog data & Digital status is suspected
5 | Chambi | 8988043148 | Shivansh AE | 104 | GPRS |  |  | ok | smchambi@hpptcl.in
6 | Pandoh | 8894813070 | Er. Lokesh (AE) | 101 | PLCC/OPGW |  |  | Ok | pandohsubstation@hpptcl.in
7 | Lahal | 9882831579 | Xen Anil Chaudhary | 104 | GPRS |  |  | Not Ok | smlahal@hpptcl.in | Not Reporting since 02.07.2021 | Analog data & Digital status is suspected
8 | Gumma | 8219104365 | Vivek AE | 104 | OPGW |  |  | Ok | smgumma@hpptcl.in
E | HPSEBL Substations
1 | Andhra | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | PLCC |  |  | Not Ok | srxen.scada@gmail.com, subldc1@gmail.com, sunitakapoorsldc@gmail.com | Not Reporting since 12.04.2021 | Analog data & Digital status is suspected
2 | Amb | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | OPGW |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com
3 | Baga | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | PLCC |  |  | Not Ok | srxen.scada@gmail.com, subldc1@gmail.com | Not Reporting since 11.05.2021 | Analog data & Digital status is suspected
4 | Kanghain | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | GPRS |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com
5 | Bajora | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | PLCC |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com
6 | Barotiwala | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | PLCC |  |  | Not Ok | srxen.scada@gmail.com, subldc1@gmail.com | Not Reporting since 17.11.2018 | Analog data & Digital status is suspected
7 | Bassi | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | OPGW |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com
8 | Bhaba | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | PLCC |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com
9 | Darlaghat | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | PLCC |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com
10 | Davni | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | GPRS |  |  | Not Ok | srxen.scada@gmail.com, subldc1@gmail.com | Not Reporting since 24.07.2018 | Analog data & Digital status is suspected
11 | Ghanavi | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | PLCC |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com
12 | Gagret | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | OPGW |  |  | Partially Ok | srxen.scada@gmail.com, subldc1@gmail.com | Not Reporting since, 22.04.2021 | ICT-3 & Luminous feeder is not reporting.
13 | Hamirpur 1 | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | PLCC |  |  | Not Ok | srxen.scada@gmail.com, subldc1@gmail.com | Not Reporting since 11.05.2021 | Analog data & Digital status is suspected
14 | Jeori | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | PLCC |  |  | Not Ok | srxen.scada@gmail.com, subldc1@gmail.com | Not Reporting since 21.06.2021 | Analog data & Digital status is suspected
15 | Kunihar | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | OPGW |  |  | Partially Ok | srxen.scada@gmail.com, subldc1@gmail.com | Not Reporting since 02.11.2018 | Digital Status of 132Kv feeders is faulty
16 | Kala Amb | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | GPRS |  |  | Not Ok | srxen.scada@gmail.com, subldc1@gmail.com | Not Reporting since 16.04.2021 | Analog data & Digital status is suspected
17 | Larji | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | OPGW |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com
18 | Mandi | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | OPGW |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com
19 | Palampur | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | PLCC |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com
20 | Solan | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | OPGW |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com
21 | Kangoo | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | OPGW |  |  | Partially Ok | srxen.scada@gmail.com, subldc1@gmail.com | Not Reporting since , 19.04.2021 | Bagga, ACC-1, ACC-2, Kunihar-1, Dehar & Hamirpur-1 feeders are suspected
22 | Kangra | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | OPGW |  |  | OK | srxen.scada@gmail.com, subldc1@gmail.com
23 | Jutogh | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | Hard Wire |  |  | OK | srxen.scada@gmail.com, subldc1@gmail.com
24 | Jasoor | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | OPGW |  |  | OK | srxen.scada@gmail.com, subldc1@gmail.com
25 | Hamirpur-2 | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | OPGW |  |  | Partially Ok | srxen.scada@gmail.com, subldc1@gmail.com | Not Reporting since 19.04.2021 | Digital status is faulty
26 | Dehra | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | OPGW |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com
27 | Baddi | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | OPGW |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com
28 | Nehrian | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | OPGW |  |  | OK | srxen.scada@gmail.com, subldc1@gmail.com
29 | Uperla Nangal | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | GPRS |  |  | Partially Ok | srxen.scada@gmail.com, subldc1@gmail.com | Not Reporting since 10.06.2018 | 220kv Baddi, wardhman, Mandhala feeders & 66Kv Nalagarh, Nalagarh-2, sunnox feeders are not reporting & Digital status is also faulty.
30 | Giri | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | OPGW |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com
31 | Binwa (GS) | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | GPRS |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com
32 | Baner (GS) | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | GPRS |  |  | Not Ok | srxen.scada@gmail.com, subldc1@gmail.com | Not Reporting since 07.01.2021 | Analog data & Digital status is suspected
33 | Gaj (GS) | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | GPRS |  |  | Not Ok | srxen.scada@gmail.com, subldc1@gmail.com | Not Reporting today i.e. 13.07.2021 | Analog data & Digital status is suspected
34 | Khauli (GS) | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | GPRS |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com
35 | Chaba (GS) | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | GPRS |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com
36 | Nogli (GS) | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | GPRS |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com
37 | Gumma (GS) | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | GPRS |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com
38 | Holi (GS) | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | GPRS |  |  | Not Ok | srxen.scada@gmail.com, subldc1@gmail.com | Not Reporting since 20.03.2021 | Analog data & Digital status is suspected
39 | Bhaba (GS) | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | GPRS |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com
F | URTDSM |  |  | 104 | Hard Wire/LAN |  |  | ok
NOTE:- (*) Currently availing Open Access
|  | Prepared By: | [5 empty] | Siemens Site Engineer
|  | Junior Engineer (SCADA) | [5 empty] | Assistant Engineer (SCADA)

## Sheet2
| Status of Internet, Recording system, SMS Pack, Screens, SCADA, EMS & Communication System | Remarks
i | SCADA Hardware | OK
ii | EMS (Energy Management System) | OK
iii | IMM (Information Model Management) | Not OK
iv | e-DNA (enterprise Distributed Network Architecture) | OK
v | Web Reporting | OK
vi | UI Server (User Interface) | OK
vii | ICCP Link (Inter centre Control Protocol) | OK