## Form-15_DTR
Frequent Single Element TRIPPING REPORT OF LINES SUMMARY
HIMACHAL PRADESH
STATE LOAD DESPATCH CENTER
Monthly Frequent Single Element Tripping Report Summary For The Month Of April 2022
Sr. No. | Date | Name of Transmission Line | Tripping Time |  | Restoration Time |  | Duration |  | Load Shedding | Reason of Tripping | Tripping due to the Element
|  |  | Hour | Minute | Hour | Minute | Hour | Minute | (MW)
1 | 2022-04-01 | 400 KV Karcham Wangtoo(JSW)-Wangto_GIS(HP) (HPPTCL) Ckt-2 | 13 | 25 | 14 | 48 | 1 | 23 | 0 | Tripping occurred on Karcham-wangtoo to evacuation of Gas in Busbar-1 of Bay 410(kala-Amb) during installation of breaker | Both the trippings were due to different kind of fault
2 | 2022-04-09 | 400 KV Karcham Wangtoo(JSW)-Wangto_GIS(HP) (HPPTCL) Ckt-2 | 18 | 43 | 20 | 25 | 1 | 42 | 0 | Wangtoo- Kala-amb ckt-1 tripped due to Y-B fault
3 | 2022-04-09 | 400 KV Kala Amb(PKTL)-Wangto_GIS(HP) (HPPTCL) Ckt-1 | 16 | 28 | 19 | 13 | 2 | 45 | 0 | Wangtoo-Kalamb ckt Tripped due to Y-B Phase Fault | Both the trippings were due to different kind of fault
4 | 2022-04-28 | 400 KV Kala Amb(PKTL)-Wangto_GIS(HP) (HPPTCL) Ckt-1 | 20 | 18 | 17 | 36 | 21 | 17 | 0 | Tripping occurred at Bay 410 (Wangtoo-kala amb ckt ). Fault parameters were checked and line maintenance team was sent for line patrolling
5 | 2022-04-09 | 400 KV Baspa(JP)-Karcham Wangtoo(JSW) (HBPCL) Ckt-1 | 16 | 33 | 18 | 10 | 1 | 37 | 0 | Both the feeders tripped as all the outgoing feeders of karcham wangtoo got tripped due to distance protection fault in outgoing feeders | Both the trippings were due to different kind of fault
6 | 2022-04-13 | 400 KV Baspa(JP)-Karcham Wangtoo(JSW) (HBPCL) Ckt-1 | 16 | 43 | 13 | 35 | 20 | 42 | 0 | Phase to Earth fault