## Sheet1
Status of healthiness of Telemetry System installed at SLDC Control Centre, Shimla as on 06.09.2022 at 11:00 AM
Sr. No. | Description | Contact Number | Contact Person | Communication |  | Speech |  | Status of Telemetry | E-Mail | Date | Remarks
|  |  |  | Protocol | Media | No. | Status
1 | 2 | 3 | 4 | 5 | 6 |  |  | 7 | 9 | 10 | 11
A | IPP's
1 | Baspa | 9805002260, 9816805258 | Ravindera Rana (DGM), Vikas Gupta (AGM) | 104 | GPRS |  |  | ok | baspa.powerhouse@jsw.in
2* | Malana HEP | 9816099653 | Mohamed Rafiq (Manager Electrical) | 101 | PLCC/OPGW |  |  | ok | malanageneration@lnjbhilwara.com
3* | Baner Sangam SHEP (Yogindra) | 7833989965 | Mr. Suraj Kumar | 101 | GPRS |  |  | Not ok | suraj452003@yahoo.co.in | Not Reporting since 02.09.2022 | Analog data & Digital status is suspected
4 | Jogini SHEP | 9805296267 | Nagasiva Reddy (plant incharge) | 104 | GPRS |  |  | ok
5* | Baragran HEP (Kanchunjunga) | 9560254005 | Prashun (plant incharge) | 104 | GPRS |  |  | ok | prasun@polyplex.com
6* | Chanju HEP | 7807878901 | D.R Sharma (Plant Head) | 104 | Lease Line/GPRS |  |  | ok | purchase.shimla@goelgroup.co.in
7 | Sumez SHEP | 9816123344 | Pushp Pev (Plant Head) | 104 | GPRS |  |  | ok | pushpdev.s@greenkogroup.com
8* | Nanti Pooling Station (33/66kV) | 9816955800 | Anil Rana (Plant incharge) | 104 | GPRS |  |  | ok | arana.shp09@gmail.com
9* | Balargha SHEP (Sandhya) | 9805073754 | Tushar Sharma (Shift Incharge) | 104 | GPRS |  |  | Ok | deepeshkumar.roy@continuumenergy.in
10* | Manuni SHEP | 7018013078 | Sanjeev mittal (GM) | 104 | GPRS |  |  | Not ok | smittal@winsometextile.com | Not Reporting since 07.07.2022 | Analog data & Digital status is suspected
11 | Brua SHEP | 7807312069 | Neerath Singh | 104 | GPRS |  |  | OK | rajcheelasingh@gmail.com
12 | Sarwari-III SHEP | 8894778734 | Inderjit (Plant Head) | 104 | GPRS |  |  | Not ok | inderjeetsharma73@yahoo.com | Not Reporting since 23.07.2021 | Analog data & Digital status is suspected
13 | Lower Aleo SHEP (Baragarh) |  |  | 104 | GPRS |  |  | ok | baragarhhydro2005@gmail.com
14 | Kota Gad SHEP | 9418073460 | Rajeev (Authorized Signatory) | 104 | GPRS |  |  | Not ok | carajeev1@gmail.com | Not Reporting today i.e. 06.09.2022 | Analog data & Digital status is suspected
15 | GR Enterprises Solar PP | 8894380675 | Mohan singh (J.E.) | 104 | GPRS |  |  | Ok | mohansinghsolarplant@gmail.com
16 | KK Kashyap Solar PP | 9818814181 | Yashveer Singh (Plant Head) | 104 | GPRS |  |  | Not Ok | kksolarpower@gmail.com | Not Reporting since 18.06.2022 | Analog data & Digital status is suspected
17 | Upper Joiner SHEP | 8894870861 | Anil (Plant Head) | 104 | GPRS |  |  | ok | somashekar.s@greenkogroup.com
18 | Lucky Brass Solar PP | 9459640219 | Sanjay Diman (Project manager) | 104 | GPRS |  |  | ok | luckybrass@rediffmail.com
19 | RP Suman | 7972744454 | RP Suman (Plant Owner) | 104 | GPRS |  |  | ok | amitlakhanpal77@gmail.com
20 | LEOND Hydro | 7018400391 | Divij (Plant Head) | 104 | GPRS |  |  | Not ok | divijsharma@jayahydro.com | Not Reporting since 22.11.2021 | Analog data & Digital status is suspected
21 | Satya Sai Hydro | 8628871917 | Anup (Plant Head) | 104 | GPRS |  |  | Not ok | akkumaranoop32@gmail.com | Not Reporting since 27.09.2021 | Analog data & Digital status is suspected
22* | Kut Hydro | 8448390088 | Rahul Kumar ( Executive IT) | 104 | GPRS |  |  | ok | kutgoodwill@kundangroup.com
23 | Jeori HEP THIPL | 8278823224 | Mr. Dheeraj Kumar | 104 | GPRS |  |  | ok | dheeraj.v@greenkogroup.com
24 | Raura Hydro | 8894752462 | Mr. Parvesh Sharma (Plant Head) | 104 | GPRS |  |  | ok | vthakur@dlz.com
25 | Siunr SHEP | 8894778734 | Varun (Plant Head) | 104 | GPRS |  |  | Not ok | usaka.varun.kullu@gmail.com | Not Reporting since 23.07.2021 | Analog data & Digital status is suspected
26 | Pinnacle Hydro | 9816307488 | Sk Bhardwaj (Plant Head) | 104 | GPRS |  |  | Not ok | skbhardwaj1@hotmail.com | Not Reporting since 19.10.2021 | Analog data & Digital status is suspected
27 | Malana- II | 9805078444 |  | 104 | GPRS |  |  | ok | anandvarma17@everestpower.in
28 | Rala (Taranda) | 9816852194 | Gopal (Plant Head) | 104 | GPRS |  |  | ok | trandapower@gmail.com
29 | Kurmi SHEP | 9816955800 | Anil Rana (Plant incharge) | 104 | GPRS |  |  | ok | arana.shp09@gmail.com
30 | Chaur | 9805519785 | Lalit (Site Engineer) | 101 | PLCC/OPGW |  |  | Not Ok | substation@everestpower.in | Not Reporting since 07.04.2022 | Analog data & Digital status is suspected
31 | Upper Nanti | 9816955800 | Anil Rana (Plant incharge) | 104 | GPRS |  |  | ok | arana.shp09@gmail.com
32 | Chanju-II | 9805651955 | Mr. Vinit Thakur | 104 | GPRS |  |  | ok | vnt.thakur@gmail.com
33 | Manorama Solar | 9465553438 | Avishek Goyal | 104 | GPRS |  |  | Ok | avishek.goyal@enepkl.com
34 | Jiwan Solar | 6284212651 | Mohit Jiwan | 104 | GPRS |  |  | Ok | avishek.goyal@enepkl.com
35 | Lower Nanti | 9816955800 | Anil Rana (Plant incharge) | 104 | GPRS |  |  | ok | arana.shp09@gmail.com
36 | Devesh Solar | 9418488996 | Sh. Ravi Rana | 104 | GPRS |  |  | ok | ranaravi99@yahoo.in
37 | Bjoli Holi | 8527190255 | Mr. Gopendera Saraswat | 104 | GPRS |  |  | ok | gopendra.saraswat@gmrgroup.in
38 | Wanger Homte | 9805649114 | Mr. Lakshmi Narayana (Project Manager) | 104 | GPRS |  |  | ok | wangerhomte@gmail.com
39 | Rajpura HEP | 8448390088 | Rahul (Site Engineer) | 104 | GPRS |  |  | ok | rajpura@kundanenergy.com
40 | Patikari HEP | 9816341220 | Mr. Shyam Lal | 104 | GPRS |  |  | ok | shyam.i@patikari.com
B | HPPCL Stations
1* | Kashang HEP | 8894321440 | Rishab (Executive Engineer) | 104 | GPRS |  |  | ok | ikhepshiftincharge@gmail.com
2 | Sainj HEP | 7018334956 | Mr. Manish Chaudhari | 104 | GPRS |  |  | ok | sm.e.sainj@gmail.com
3 | Berra Dol Solar | 7018301778 | Anil Kumar (JE) | 101 | GPRS |  |  | Ok | gm_generation@hppcl.in
4 | Sawra Kuddu | 9418340530 | Rajneesh Kumar | 104 | OPGW |  |  | ok | dgmelectrical.skhep@gmail.com
C | Open Access Consumers
1* | ACC Barmana, Kangoo | 9816016936 | Tara Sharma (Plant incharge) | 104 | GPRS |  |  | Ok | tara.sharma@acclimited.com
2* | Ambuja Cement (Rauri) | 981602351, 9805009602 | Rohit kumar, Kishori lal (AE darla) | 104 | GPRS |  |  | ok | deepak.dhiman@ambujacement.com
3* | Ultra-Tech Cement, Bagga | 9805002920 | Mr. ID Prasad | 101 | PLCC |  |  | Not ok | naveen.kagrawal@adityabirla.com | Not Reporting since 11.08.2022 | Analog data & Digital status is suspected
4* | Birla Textile, Baddi | 9318760937 | Ramesh Mishra (plant incharge) | 104 | GPRS |  |  | Ok | msarora@sutlejtextiles.com
5* | Winsome I, Baddi | 7018013078 | Sanjeev mittal (GM) | 104 | GPRS |  |  | Ok | smittal@winsometextile.com
6* | Ultra-Tech Cement, Bageri | 9805375871 | N.S Rawat (AE) | 104 | GPRS |  |  | Ok | ashwani.kumar@adityabirla.com
7* | Ambuja Cement (Nalagarh) | 9418075526, 9815609789 | Devraj, Alok Sharma (DGM) | 104 | GPRS |  |  | Ok | deepak.dhiman@ambujacement.com
8* | Ambuja Cement (Sulli) | 981602351, 9805009602 | Rohit kumar, Kishori lal (AE darla) | 104 | GPRS |  |  | Ok | kishori.sharma@ambujacement.com
9* | Loreal India Pvt. Ltd. Baddi | 7066091562 | Mr. Avinash Yadav | 104 | GPRS |  |  | Ok | Avinash.yadav2@loreal.com, Shruti.mathur@loreal.com
D | HPPTCL Stations
1 | Phojal | 7018333984 | Vimal Thakur (AE) | 101 | PLCC/OPGW |  |  | ok | smphojal.tcl@hpmail.in
2 | Karian | 9805413394 | Er. Kanav (AE) | 104 | GPRS |  |  | ok | smchamba.tcl@hpmail.in
3 | Bhoktoo | 9816698731 | Dilip Kumar (JE) | 104 | GPRS |  |  | ok | smbhaba.tcl@hpmail.in
4 | Wangtoo | 8628829397 | Ishita (AE) | 104 | GPRS |  |  | ok | smbhaba.tcl@hpmail.in
5 | Chambi | 8988043148 | Shivansh AE | 104 | GPRS |  |  | ok | smchambi.tcl@hpmail.in |  |  |  |  | s
6 | Pandoh | 8894813070 | Er. Lokesh (AE) | 104 | OPGW |  |  | OK | smsarabai.tcl@hpmail.in
7 | Lahal | 8219493212 | Er. Surrender (AE) | 104 | GPRS |  |  | Partially Ok | smlahal1.tcl@hpmail.in, smlahal.tcl@hpmail.in | Not Reporting since 05.09.2022 | Digital status is suspected
8 | Gumma | 8219104365 | Vivek AE | 104 | OPGW |  |  | Ok | smgumma.tcl@hpmail.in
9 | Urni | 9816257782 |  | 104 | GPRS |  |  | ok | urniss.tcl@hpmail.in
10 | Hatkoti | 9882184409 | Mohit Sharma AE | 104 | OPGW |  |  | ok | smrohru.tcl@hpmail.in
11 | Sunda | 7018333984 | Er. Vimal AE | 104 | GPRS |  |  | ok | vimal.t.tcl@hpmail.in
12 | Dehan | 8219493212 | Er. Surrendra AE | 104 | GPRS |  |  | Ok | parikshit.tcl@hpmail.in
E | HPSEBL Substations
1 | Andhra | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | OPGW |  |  | Not Ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com | Not Reporting since 03.09.2022 | Analog data & Digital status is suspected
2 | Amb | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | OPGW |  |  | Not Ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com | Not Reporting since 23.06.2022 | Analog data & Digital status is suspected
3 | Baga | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | PLCC |  |  | Not Ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com | Not Reporting since 11.08.2022 | Analog data & Digital status is suspected | Not Reporting since 18.02.2022 | Digital Data is faulty.
4 | Kanghain | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | GPRS |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com
5 | Bajora | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | OPGW |  |  | OK | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com
6 | Barotiwala | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | PLCC |  |  | Not Ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com | Not Reporting since 17.11.2018 | Analog data & Digital status is suspected
7 | Bassi | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | OPGW |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com
8 | Bhaba | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | PLCC |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com
9 | Darlaghat | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | PLCC |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com
10 | Davni | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | GPRS |  |  | Not Ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com | Not Reporting since 24.07.2018 | Analog data & Digital status is suspected
11 | Ghanavi | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | PLCC |  |  | Not Ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com | Not Reporting since 10.08.2022 | Analog data & Digital status is suspected
12 | Gagret | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | OPGW |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com
13 | Hamirpur 1 | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | PLCC |  |  | Not Ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com | Not Reporting since 11.05.2021 | Analog data & Digital status is suspected
14 | Jeori | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | PLCC |  |  | ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com
15 | Kunihar | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | OPGW |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com
16 | Kala Amb | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | GPRS |  |  | Not Ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com | Not Reporting since 01.07.2022 | Analog data & Digital status is suspected
17 | Larji | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | OPGW |  |  | Not ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com | Not Reporting since 11.08.2022 | Analog data & Digital status is suspected
18 | Mandi | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | OPGW |  |  | Partially Ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com | Not Reporting since 01.11.2021 | Real Time data is reporting faulty values
19 | Palampur | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | PLCC |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com
20 | Solan | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | OPGW |  |  | Not ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com | Not Reporting since 29.08.2022 | Analog data & Digital status is suspected
21 | Kangoo | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | OPGW |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com
22 | Kangra | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | OPGW |  |  | Not Ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com | Not Reporting since 31.05.2022 | Analog data & Digital status is suspected
23 | Jutogh | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | Hard Wire |  |  | OK | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com
24 | Jasoor | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | OPGW |  |  | OK | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com
25 | Hamirpur-2 | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | OPGW |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com
26 | Dehra | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | OPGW |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com
27 | Baddi | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | OPGW |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com
28 | Rakkar (UNA) | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | OPGW |  |  | Not Ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com | Not Reporting since 21.06.2022 | Analog data & Digital status is suspected
29 | Nehrian | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | OPGW |  |  | Ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com
30 | Uperla Nangal | 9318691741 | Khoob Ram Sharma (A.E.) | 101 | GPRS |  |  | Partially Ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com | Not Reporting since 10.06.2018 | 220kv Baddi, wardhman, Mandhala feeders & 66Kv Nalagarh, Nalagarh-2, sunnox feeders are not reporting & Digital status is also faulty.
31 | Giri | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | OPGW |  |  | Partially ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com | Not Reporting since 10.08.2020 | Data is intermittent
32 | Binwa (GS) | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | GPRS |  |  | ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com
33 | Baner (GS) | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | GPRS |  |  | ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com
34 | Gaj (GS) | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | GPRS |  |  | ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com
35 | Khauli (GS) | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | GPRS |  |  | ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com
36 | Chaba (GS) | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | GPRS |  |  | Not ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com | Not Reporting since 10.08.2022 | Analog data & Digital status is suspected
37 | Nogli (GS) | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | GPRS |  |  | ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com
38 | Gumma (GS) | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | GPRS |  |  | ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com
39 | Holi (GS) | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | GPRS |  |  | Not ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com | Not Reporting since 10.08.2022 | Analog data & Digital status is suspected
40 | Bhaba (GS) | 9318691741 | Khoob Ram Sharma (A.E.) | 104 | GPRS |  |  | ok | srxen.scada@gmail.com, subldc1@gmail.com, pcshimla2003@gmail.com, xen.plccsnr@gmail.com, aeplccshimla@gmail.com
F | URTDSM |  |  | 104 | Hard Wire/LAN |  |  | ok
NOTE:- (*) Currently availing Open Access
|  | Prepared By: | [5 empty] | Siemens Site Engineer
|  | Junior Engineer (SCADA) | [5 empty] | Assistant Engineer (SCADA)

## Sheet2
| Status of Internet, Recording system, SMS Pack, Screens, SCADA, EMS & Communication System | Remarks
i | SCADA Hardware | OK
ii | EMS (Energy Management System) | OK
iii | IMM (Information Model Management) | Not OK
iv | e-DNA (enterprise Distributed Network Architecture) | OK
v | Web Reporting | OK
vi | UI Server (User Interface) | OK
vii | ICCP Link (Inter centre Control Protocol) | OK