## Report_PSPR NRLDC SLDC
File Name: PSPR- |  |  | 2023-05-04
Hiamchal Pradesh State Load Despatch Centre
[18 empty] | DATED | 2023-05-05
FROM | [15 empty] | TO
| POWER CONTROLLER | [16 empty] | D.G.M.,NRLDC,NEW DELHI
| HPSLDC, GoHP, Totu, Shimla-11 | [16 empty] | FAX # 011-26852747-26853082
(FAX #: 0177 2837543)
|  |  | DEMAND AND POWER SUPPLY POSITION | [18 empty] | DEMAND OF STATE |  |  | 28579.5 | MWh
[22 empty] | ACTUAL MALANA GENERATION |  |  | 702 | MWh
|  | State:- Himachal Pradesh | [19 empty] | ACTUAL BASPA GENERATION |  |  | 1435 | MWh | MALANA-II | 589 | MWh |  |  |  |  | SN | Time Block | Frequency | Avg. Freq. | Demand | Avg Demand
[18 empty] | PEAK DEMAND(MW) |  | 1583 | [6 empty] | HOLI BAJOLI | 2343 | MWh |  |  |  |  | 1 | 00.00-00.15 | 49.99 |  | 907
|  | Month/Day :- |  |  |  |  | 2023-05-04 | [10 empty] | Min.DEMAND(MW) |  | 841 |  | ACTUAL OWN GENERATION |  |  | 14495.694 | MWh | SWARA KUDDU | 1356 | MWh |  |  |  |  | 2 | 00.15-00.30 | 49.93 |  | 901
[34 empty] | 3 | 00.30-00.45 | 49.95 |  | 910 |  | for VLOOKUP(MaxGenHrs.)
HRS. OF THE DAY | GENERATION (MW) | [6 empty] | NET IMPORT (MW) | DEMAND MET (MW) | FREQ-UENCY CORREC-TION (MW) | DEMAND NOT MET | [7 empty] | TOTAL DEMAND NOT MET (MW) | TOTAL ENERGY EQUIVA-LENT TO DEMAND NOT MET (MU) | TOTAL UNRESTRI-CTED DEMAND (MW) P7=P1+P2+P11 | HRS. OF THE DAY | GENERATION (MW) |  |  |  | AVERAGE DEMAND MET (MW) | MAX DEMAND (HOURLY) | MIN DEMAND (HOURLY) | DEMAND ADJUSTMENT(MAXIMUM/MINIMUM/AVERAGE) | CALCULATION MAX/MIN ACTUAL | DEMAND TREND | DUE TO LOAD SHEDD-ING (MW) | 4 | 00.45-01.00 | 49.97 | 49.96 | 908 | 906.5 | Malana | HRS. OF THE DAY | TIME | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | TOTAL
[11 empty] | Low Availability (in MW) | Financial Constraints (in MW) | Emergency load shedding due to security and reliability of the Grid-over Drawl (in MW) | Planned maintenance in transmission system (in MW) | Transmission constraint (in MW) | Planned maintenance in distribution system (in MW) | Distribution constraints (in MW) | Any other reasion ( to be specfied) (MW) | [15 empty] | 5 | 01.00-01.15 | 49.98 |  | 911 |  |  |  | MALANA-2 | 25 | 25 | 25 | 25 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.25 | 30 | 30.25 | 42 | 100.5 | 100.25 | 98.25 | 29.5 | 30 | 587.5
[34 empty] | 6 | 01.15-01.30 | 50 |  | 909 |  |  |  | SWARA KUDDU | 74 | 74 | 74 | 74 | 37.5 | 37 | 37 | 37 | 37 | 65.75 | 74 | 74 | 74 | 74 | 74 | 1.25 | 0 | 0.75 | 65.5 | 74 | 74 | 74 | 74 | 74 | 1354.75
[34 empty] | 7 | 01.30-01.45 | 49.99 |  | 902
[34 empty] | 8 | 01.45-02:00 | 49.99 | 49.99 | 882 | 901
| OWN GEN | Malana | BASPA | MALANA-II | SAWRA KUDDU | BAJOLI HOLI | TOTAL | [15 empty] | OWN Generation | Malana | BASPA | TOTAL | [7 empty] | 9 | 02.00-02.15 | 49.99 |  | 881 |  | Malana
[9 empty] | 5+6 | [24 empty] | 10 | 02.15-02.30 | 49.99 |  | 871
[9 empty] | P1 | P2 | P3 | P4 | P5 | P6 | P7 | P8 | P9 | P10 | P11 | P11/1000 | P12 | [5 empty] | P1 | [5 empty] | P3 | 11 | 02.30-02.45 | 50.02 |  | 870
1 | 2 | 3 | 4 | 5 | 6 |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 7 | 8 | 9 | 10 | 12 | 02.45-03:00 | 50.01 | 50.0025 | 849 | 867.75
1 | 681.8806 | 60.0651 | 30.2849 | 25 | 74 | 122 | 993.2305 | -86.8574 | 906.3731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 906.3731 | 1 | 692.4167 | 59.5 | 30 | 781.9167 | 906.5 | 910 | 901 | 906.5 | 906.5 | 906.3731 | 0 | 13 | 03.00-03.15 | 49.99 |  | 844 |  | 59.5 | 1
2 | 671.5403 | 59.5603 | 30.2849 | 25 | 74 | 122 | 982.3856 | -81.5116 | 900.8739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900.8739 | 2 | 681.9167 | 59 | 30 | 770.9167 | 901 | 911 | 882 | 901 | 901 | 900.8739 | 0 | 14 | 03.15-03.30 | 50.01 |  | 841 |  | 59 | 2
3 | 615.5308 | 59.0556 | 36.0895 | 25 | 74 | 122 | 931.6759 | -64.0473 | 867.6286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 867.6286 | 3 | 625.0417 | 58.5 | 35.75 | 719.2917 | 867.75 | 881 | 849 | 867.75 | 867.75 | 867.6286 | 0 | 15 | 03.30-03.45 | 50.02 |  | 859 |  | 58.5 | 3
4 | 589.8033 | 0.25237 | 39.8751 | 25 | 74 | 122 | 850.9308 | -9.9308 | 841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 841 | 4 | 598.9167 | 0.25 | 39.5 | 638.6667 | 850.25 | 859 | 841 | 841 | 841 | 841 | 0 | 16 | 03.45-04.00 | 50.01 | 50.0075 | 857 | 850.25 | 0.25 | 4
5 | 609.9667 | 0 | 52.4938 | 24.5 | 37.5 | 112 | 836.4606 | 58.9141 | 895.3747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 895.3747 | 5 | 619.3917 | 0 | 52 | 671.3917 | 895.5 | 929 | 862 | 895.5 | 895.5 | 895.3747 | 0 | 17 | 04.00-04.15 | 49.99 |  | 862 |  | 0 | 5
6 | 664.6961 | 0 | 87.3215 | 0 | 37 | 112 | 901.0176 | 195.5789 | 1096.5965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1096.5965 | 6 | 674.9667 | 0 | 86.5 | 761.4667 | 1096.75 | 1256 | 953 | 1096.75 | 1096.75 | 1096.5965 | 0 | 18 | 04.15-04.30 | 49.98 |  | 892 |  | 0 | 6
7 | 717.1358 | 0 | 110.2875 | 0 | 37 | 112 | 976.4234 | 478.1231 | 1454.5464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1454.5464 | 7 | 728.2167 | 0 | 109.25 | 837.4667 | 1454.75 | 1535 | 1344 | 1454.75 | 1454.75 | 1454.5464 | 0 | 19 | 04.30-04.45 | 49.98 |  | 899 |  | 0 | 7
8 | 609.2281 | 0 | 81.7693 | 0 | 37 | 112 | 839.9974 | 743.0026 | 1583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1583 | 8 | 618.6417 | 0 | 81 | 699.6417 | 1569.75 | 1583 | 1557 | 1583 | 1583 | 1583 | 0 | 20 | 04.45-05.00 | 49.97 | 49.98 | 929 | 895.5 | 0 | 8
9 | 567.6949 | 0 | 40.1275 | 0 | 37 | 99.75 | 744.5724 | 771.7154 | 1516.2878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1516.2878 | 9 | 576.4667 | 0 | 39.75 | 616.2167 | 1516.5 | 1522 | 1502 | 1516.5 | 1516.5 | 1516.2878 | 0 | 21 | 05.00-05.15 | 49.96 |  | 953 |  | 0 | 9
10 | 578.7245 | 0 | 30.2849 | 0 | 65.75 | 99.75 | 774.5094 | 698.0345 | 1472.5439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1472.5439 | 10 | 587.6667 | 0 | 30 | 617.6667 | 1472.75 | 1480 | 1452 | 1472.75 | 1472.75 | 1472.5439 | 0 | 22 | 05.15-05.30 | 49.93 |  | 1025 |  | 0 | 10
11 | 598.1739 | 0 | 54.5128 | 0 | 74 | 100 | 826.6868 | 568.8679 | 1395.5547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1395.5547 | 11 | 607.4167 | 0 | 54 | 661.4167 | 1395.75 | 1420 | 1369 | 1395.75 | 1395.75 | 1395.5547 | 0 | 23 | 05.30-05.45 | 49.93 |  | 1153 |  | 0 | 11
12 | 624.0245 | 0 | 93.3785 | 0 | 74 | 90.75 | 882.153 | 497.154 | 1379.307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1379.307 | 12 | 633.6667 | 0 | 92.5 | 726.1667 | 1379.5 | 1392 | 1367 | 1379.5 | 1379.5 | 1379.307 | 0 | 24 | 05.45-06.00 | 49.92 | 49.935 | 1256 | 1096.75 | 0 | 12
13 | 618.362 | 0 | 93.3785 | 0 | 74 | 81 | 866.7405 | 441.5764 | 1308.3169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1308.3169 | 13 | 627.9167 | 0 | 92.5 | 720.4167 | 1308.5 | 1347 | 1218 | 1308.5 | 1308.5 | 1308.3169 | 0 | 25 | 06.00-06.15 | 49.99 |  | 1344 |  | 0 | 13
14 | 554.745 | 0 | 65.3649 | 0 | 74 | 81 | 775.1099 | 444.2194 | 1219.3293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1219.3293 | 14 | 563.3167 | 0 | 64.75 | 628.0667 | 1219.5 | 1231 | 1209 | 1219.5 | 1219.5 | 1219.3293 | 0 | 26 | 06.15-06.30 | 50 |  | 1434 |  | 0 | 14
15 | 649.8012 | 0 | 111.0447 | 0 | 74 | 81.25 | 916.0959 | 316.2316 | 1232.3275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1232.3275 | 15 | 659.8417 | 0 | 110 | 769.8417 | 1232.5 | 1245 | 1213 | 1232.5 | 1232.5 | 1232.3275 | 0 | 27 | 06.30-06.45 | 50.03 |  | 1506 |  | 0 | 15
16 | 614.9891 | 0 | 83.7883 | 2.25 | 1.25 | 81 | 783.2774 | 446.8005 | 1230.0778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1230.0778 | 16 | 624.4917 | 0 | 83 | 707.4917 | 1230.25 | 1247 | 1211 | 1230.25 | 1230.25 | 1230.0778 | 0 | 28 | 06.45-07.00 | 50.03 | 50.0125 | 1535 | 1454.75 | 0 | 16
17 | 596.0567 | 39.8751 | 60.5698 | 30 | 0 | 81 | 807.5016 | 448.3226 | 1255.8242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1255.8242 | 17 | 605.2667 | 39.5 | 60 | 704.7667 | 1256 | 1263 | 1245 | 1256 | 1256 | 1255.8242 | 0 | 29 | 07.00-07.15 | 50.02 |  | 1567 |  | 39.5 | 17
18 | 555.9267 | 40.3799 | 60.5698 | 30.25 | 0.75 | 81 | 768.8764 | 421.207 | 1190.0834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1190.0834 | 18 | 564.5167 | 40 | 60 | 664.5167 | 1190.25 | 1225 | 1169 | 1190.25 | 1190.25 | 1190.0834 | 0 | 30 | 07.15-07.30 | 50.01 |  | 1583 |  | 40 | 18
19 | 520.7207 | 41.137 | 43.156 | 42 | 65.5 | 81 | 793.5137 | 381.3218 | 1174.8356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1174.8356 | 19 | 528.7667 | 40.75 | 42.75 | 612.2667 | 1175 | 1181 | 1169 | 1175 | 1175 | 1174.8356 | 0 | 31 | 07.30-07.45 | 50.04 |  | 1572 |  | 40.75 | 19
20 | 551.7414 | 87.5739 | 68.141 | 100.5 | 74 | 81 | 962.9563 | 297.1173 | 1260.0736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1260.0736 | 20 | 560.2667 | 86.75 | 67.5 | 714.5167 | 1260.25 | 1302 | 1207 | 1260.25 | 1260.25 | 1260.0736 | 0 | 32 | 07.45-08.00 | 50.05 | 50.03 | 1557 | 1569.75 | 86.75 | 20
21 | 622.892 | 87.8262 | 51.9891 | 100.25 | 74 | 101.5 | 1038.4574 | 215.3672 | 1253.8245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1253.8245 | 21 | 632.5167 | 87 | 51.5 | 771.0167 | 1254 | 1276 | 1220 | 1254 | 1254 | 1253.8245 | 0 | 33 | 08.00-08.15 | 50 |  | 1520 |  | 87 | 21
22 | 625.6002 | 86.8167 | 33.3134 | 98.25 | 74 | 102 | 1019.9803 | 127.1091 | 1147.0895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1147.0895 | 22 | 635.2667 | 86 | 33 | 754.2667 | 1147.25 | 1196 | 1104 | 1147.25 | 1147.25 | 1147.0895 | 0 | 34 | 08.15-08.30 | 49.99 |  | 1522 |  | 86 | 22
23 | 533.0305 | 86.8167 | 30.2849 | 29.5 | 74 | 101.75 | 855.3822 | 184.9722 | 1040.3544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1040.3544 | 23 | 541.2667 | 86 | 30 | 657.2667 | 1040.5 | 1077 | 1012 | 1040.5 | 1040.5 | 1040.3544 | 0 | 35 | 08.30-08.45 | 50.02 |  | 1522 |  | 86 | 23
24 | 523.4289 | 59.8127 | 46.6892 | 30 | 74 | 91 | 824.9308 | 133.685 | 958.6158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 958.6158 | 24 | 531.5167 | 59.25 | 46.25 | 637.0167 | 958.75 | 983 | 943 | 958.75 | 958.75 | 958.6158 | 0 | 36 | 08.45-09.00 | 50.1 | 50.0275 | 1502 | 1516.5 | 59.25 | 24
[34 empty] | 37 | 09.00-09.15 | 50.05 |  | 1480
TOTAL (in MWh) | 14495.694 | 709.1716 | 1435 | 587.5 | 1354.75 | 2370.75 | 20952.8656 | 7626.9736 | 28579.8392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28579.8392 | TOTAL | 14719.675 | 702.5 | 1421.5 | 16843.675 | 28579.5 |  |  | 28583.5 | 28583.5 | 28579.8392 | 0 | 38 | 09.15-09.30 | 50.01 |  | 1480
[34 empty] | 39 | 09.30-09.45 | 50.06 |  | 1479
[34 empty] | 40 | 09.45-10.00 | 50.03 | 50.0375 | 1452 | 1472.75
|  |  | Hourly Average Frequency (Fr) |  |  |  | 5+6 P4 12: 49.9951; 5+6 P6 14: HZ | Note :- Please don't edit these figures. | [11 empty] | 41 | 10.00-10.15 | 50.02 |  | 1420
|  |  | Demand met for the day |  |  |  | 5+6 P4 12: 1583; 5+6 P6 14: MW | [12 empty] | 42 | 10.15-10.30 | 49.98 |  | 1411
|  |  | Unrestricted Demand for the day |  |  |  | 5+6 P4 12: 1583; 5+6 P6 14: MW | MAX = | 1583 | [10 empty] | 43 | 10.30-10.45 | 49.96 |  | 1369
|  |  | Minimum Demand(Unrestricted) for the day |  |  |  | 5+6 P4 12: 841; 5+6 P6 14: MW; 5+6 P11 19: Aux.; 5+6 P11/1000 20: Net gen. | MIN = | 841 | [10 empty] | 44 | 10.45-11.00 | 49.98 | 49.985 | 1383 | 1395.75
|  |  | Gross own generation |  |  |  | 5+6 P4 12: 14495.694; 5+6 P6 14: MWH; 5+6 P11 19: 30.116; 5+6 P11/1000 20: 14465.578 | [12 empty] | 45 | 11.00-11.15 | 50.03 |  | 1392
|  |  | Gross Baspa generation |  |  |  | 5+6 P4 12: 1435; 5+6 P6 14: MWH; 5+6 P11 19: 4.98; 5+6 P11/1000 20: 1430.02 | [12 empty] | 46 | 11.15-11.30 | 50.04 |  | 1379
|  |  | Gross Malana generation |  |  |  | 5+6 P4 12: 709.1716; 5+6 P6 14: MWH; 5+6 P11 19: 1.054; 5+6 P11/1000 20: 708.1176 | [12 empty] | 47 | 11.30-11.45 | 50.01 |  | 1380
|  |  | Malana generation at 0300 Hrs. |  |  |  | 5+6 P4 12: 58.5; 5+6 P6 14: MW | [12 empty] | 48 | 11.45-12.00 | 50 | 50.02 | 1367 | 1379.5
|  |  | Malana generation at 2400 Hrs. |  |  |  | 5+6 P4 12: 59.25; 5+6 P6 14: MW | [12 empty] | 49 | 12.00-12.15 | 50.02 |  | 1347
|  |  | Max.generation of Malana at 2100 Hrs. |  |  |  | 5+6 P4 12: 87; 5+6 P6 14: MW | [12 empty] | 50 | 12.15-12.30 | 49.98 |  | 1308
[7 empty] | 5+6 P2 10: Off Peak Hrs MW; 5+6 P4 12: Peak Hrs MW; 5+6 P11 19: Gross Lus; 5+6 P11/1000 20: Net Lus | [14 empty] | 49.98 |  | 1302
|  |  | Total Own Generation |  |  |  | 5+6 P2 10: 619.8729; 5+6 P4 12: 736.9223; 5+6 P11 19: 144.9569; 5+6 P11/1000 20: 144.6558 | [12 empty] | 51 | 12.30-12.45 | 49.95 | 49.9825 | 1277 | 1308.5
|  |  | Above 25 MW |  |  |  | 5+6 P2 10: 243.6348; 5+6 P4 12: 200.3678; 5+6 P11 19: 58.578; 5+6 P11/1000 20: 58.3294 | [12 empty] | 52 | 12.45-13.00 | 50.03 |  | 1218
|  |  | Below 25 MW(Small Hydro <25 MW) |  |  |  | 5+6 P2 10: 376.2381; 5+6 P4 12: 536.5546; 5+6 P11 19: 86.379; 5+6 P11/1000 20: 86.3263 | [12 empty] | 53 | 13.00-13.15 | 49.98 |  | 1220
[34 empty] | 55 | 13.30-13.45 | 49.92 |  | 1231
[34 empty] | 56 | 13.45-14.00 | 49.84 | 49.9425 | 1209 | 1219.5
[7 empty] | 5+6 P11 19: Shift Incharge | [12 empty] | 57 | 14.00-14.15 | 49.91 |  | 1213
[7 empty] | 5+6 P11 19: HPSLDC, GoHP, Totu,Shimla-11. | [12 empty] | 58 | 14.15-14.30 | 49.75 |  | 1233
Load Shedding For Dated | [6 empty] | 5+6 P1 9: 2023-05-04 | [12 empty] | 59 | 14.30-14.45 | 49.93 |  | 1245
[34 empty] | 60 | 14.45-15.00 | 50.01 | 49.9 | 1239 | 1232.5 | bar: 7 to 5+6 P4 12; 5+6 P12 21
SR.NO. | NAME OF FEEDER / SubStation | LOAD IN MW |  |  | TIME PERIOD |  | 5+6 P1 9: DURATION; 5+6 P3 11: LOAD SHEDDING IN LUS; 5+6 P4 12: REASON | [12 empty] | 61 | 15.00-15.15 | 50.05 |  | 1211
|  | BEFORE SHEDD-ING | AFTER SHEDD-ING | LOAD SHEDD-ING | FROM | [28 empty] | 62 | 15.15-15.30 | 50.03 |  | 1230 | bar: 7 to 5+6 P4 12; 5+6 P12 21
[5 empty] | Hour | Minute | 7: Hour; 8: Minute; 5+6 P1 9: Hour; 5+6 P2 10: Minute | [12 empty] | 63 | 15.30-15.45 | 49.99 |  | 1233
1 | 2 | 3 | 4 | 5 | 6 | 7 | 7: 8; 8: 9; 5+6 P1 9: 10; 5+6 P2 10: 11; 5+6 P3 11: 12; 5+6 P4 12: 13 | [12 empty] | 64 | 15.45-16.00 | 49.99 | 50.015 | 1247 | 1230.25
1 | [33 empty] | 65 | 16.00-16.15 | 49.95 |  | 1263 | bar: 5+6 P12 21
2 | [33 empty] | 66 | 16.15-16.30 | 50 |  | 1260 | bar: 5+6 P12 21
3 | [33 empty] | 67 | 16.30-16.45 | 49.99 |  | 1256 | bar: 5+6 P12 21
4 | [33 empty] | 68 | 16.45-17.00 | 50 | 49.985 | 1245 | 1256 | bar: 5+6 P12 21
5 | [33 empty] | 69 | 17.00-17.15 | 50.03 |  | 1225 | bar: 5+6 P12 21
6 | [33 empty] | 70 | 17.15-17.30 | 50.02 |  | 1195 | bar: 5+6 P12 21
7 | [33 empty] | 71 | 17.30-17.45 | 50.02 |  | 1172 | bar: 5+6 P12 21
8 | [33 empty] | 72 | 17.45-18.00 | 50.04 | 50.0275 | 1169 | 1190.25 | bar: 5+6 P12 21
[34 empty] | 73 | 18.00-18.15 | 50.04 |  | 1173 | bar: 5+6 P12 21
[34 empty] | 74 | 18.15-18.30 | 50.03 |  | 1169 | bar: 5+6 P12 21
[34 empty] | 75 | 18.30-18.45 | 50.04 |  | 1181 | bar: 5+6 P12 21
[34 empty] | 76 | 18.45-19.00 | 50.03 | 50.035 | 1177 | 1175 | bar: 5+6 P12 21
[34 empty] | 77 | 19.00-19.15 | 50.01 |  | 1207 | bar: 5+6 P12 21
[34 empty] | 78 | 19.15-19.30 | 50 |  | 1253 | bar: 5+6 P12 21
[34 empty] | 79 | 19.30-19.45 | 50.03 |  | 1279 | bar: 5+6 P12 21
[34 empty] | 80 | 19.45-20.00 | 50.01 | 50.0125 | 1302 | 1260.25 | bar: 5+6 P12 21
[34 empty] | 81 | 20.00-20.15 | 50.01 |  | 1276 | bar: 5+6 P12 21
[34 empty] | 82 | 20.15-20.30 | 49.98 |  | 1271 | bar: 5+6 P12 21
[34 empty] | 83 | 20.30-20.45 | 49.97 |  | 1249 | bar: 5+6 P12 21
[34 empty] | 84 | 20.45-21.00 | 49.95 | 49.9775 | 1220 | 1254 | bar: 5+6 P12 21
[34 empty] | 85 | 21.00-21.15 | 49.92 |  | 1196 | bar: 5+6 P12 21
[34 empty] | 86 | 21.15-21.30 | 49.9 |  | 1155 | bar: 5+6 P12 21
[34 empty] | 87 | 21.30-21.45 | 49.97 |  | 1134
[34 empty] | 88 | 21.45-22.00 | 50.02 | 49.9525 | 1104 | 1147.25
[34 empty] | 89 | 22.00-22.15 | 49.98 |  | 1077
[34 empty] | 90 | 22.15-22.30 | 50.03 |  | 1046
[34 empty] | 91 | 22.30-22.45 | 50.06 |  | 1027
[34 empty] | 92 | 22.45-23.00 | 50.06 | 50.0325 | 1012 | 1040.5
[34 empty] | 93 | 23.00-23.15 | 50.03 |  | 983
[34 empty] | 94 | 23.15-23.30 | 50.02 |  | 960
[34 empty] | 95 | 23.30-23.45 | 50.04 |  | 949
[34 empty] | 96 | 23.45-24.00 | 50.04 | 50.0325 | 943 | 958.75
[35 empty] | Total | 49.9951 | 49.9951 | 28579.5 | 28579.5
[35 empty] | max | 1583 |  | avg. max | 1569.75
[35 empty] | min | 841 |  | avg. min | 850.25
Note on AG16: ReportServer: critical formulas…….do not disturb
Note on AH16: ReportServer: critical formulas…….do not disturb
Note on Y24: Please don't edit here
Note on H25: Column no. 5 =Sum (2+3+4 Column)
Note on L25: The fig of power cut comes from daily hourly load sheet.