## Report_DPS (HPSLDC)
| File Name: DAILY POWER SUPPLY- | 2024-04-18
Hiamchal Pradesh State Load Despatch Centre
Government of Himahcal Pradesh
|  | E-Mail sehpsldc@gmail.com |  |  |  |  | Dated | 2024-04-19
FROM: |  |  |  | TO
| POWER CONTROLLER |  |  |  | Managing Director
| HPSLDC, GoHP, Totu, Shimla-11 |  |  |  | HP State Load Despatch Centre
| (FAX #: 0177 2837543) |  |  |  | Govt. of HP, Totu, Shimla-11
Eamail:mdhpsldc@gmail.com
Subject:- Daily Power Supply Position For Dated |  |  | 2024-04-18
Sir,
The daily Power Supply Position is tabulated as under :-
S.No. | POWER HOUSES UNDER HPSEBL | INSTALLED CAPACITY (MW) | DAILY GENERATION TARGET ON YEARLY BASIS [CE (Gen)/IPP] Lakh Units | DAILY GENERATION TARGET ON WEEKLY BASIS (SLDC) LU on Previous year Trend | ESTIMATED GENERATION ON DAYAHEAD BASIS FROM HPSEBL P/ H's / IPP) Lakh Units | ACTUAL (Lakh Units) | MAX Gen. Mega Watts | REMARKS | [7 empty] | 12.833
( Reason for Major Variation)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | LARJI (3x42 MW) | 126 | 23.19 | 23.19 | 0 | 0 | 0
2 | BHABA (3x40 MW) | 120 | 19.2 | 19.2 | 7.32 | 9.22 | 77
3 | BASSI (4x16.50MW) | 66 | 9.8 | 9.8 | 11.1975 | 14.106 | 66
4 | GIRI (2x30 MW) | 60 | 0.73 | 0.73 | 2.115 | 1.86 | 30
5 | GANVI-I(2x11.25 MW) | 22.5 | 4.07 | 4.07 | 1.0975 | 0.352 | 7.8
6 | ANDHRA (3x5.65 MW) | 16.95 | 1.71 | 1.71 | 1.2 | 1.5822 | 10
7 | BANER (3x4 MW) | 12 | 0.87 | 0.87 | 1.8725 | 1.1874 | 6.1
8 | KHAULI (2x6 MW) | 12 | 0.81 | 0.81 | 1.8725 | 2.574 | 12
9 | GAJ ( 3x3.5 MW) | 10.5 | 0.92 | 0.92 | 1.2 | 1.4554 | 6.528
10 | GANVI-II(2x5) | 10 | 2.41 | 2.41 | 1.745 | 0.97759 | 5
11 | BINWA (2x3 MW) | 6 | 0.73 | 0.73 | 0.12 | 0.70245 | 3
12 | THIROT (3x1.5 MW) | 4.5 | 0.25 | 0.25 | 0.12 | 0 | 0 |  | Anticipated/ Estimated Generation |  |  | 82.2503
13 | MINI/MICRO ** (30.95 MW) | 30.95 | 1.53 | 1.52 | 0.2544 | 2.12
A | TOTAL HPSEBL Gen.(1 to 12) | 497.4 | 66.22 | 66.21 | 30.1144 | 36.137 | 223.428 |  | Total actual Gen. |  |  | 116.0624
B | IPP's Generation |  |  |  |  | Actual Availed by HPSEBL |  | Total Generation of Baspa-II in LUs
i) | Baspa (3 X100MW) IPP
| (a) 88% | 300 | 10.56 | 8.2896 | 8.932 | 8.881 | 200 | 10.092
| (b) 12% |  | 1.44 | 1.1304 | 1.218 | 1.211 |  | Total Generation of Malana
ii) | Malana (2X43 MW) IPP HP Share (20%) | 86 | 0.446 | 0.646 | 0.93428 | 1.186 | 45 | 5.93
Total Generation of IPP's selling out side in Lus
26.3429
iii) | KASHANG (3x65 MW) | 195 | 0 | 0 | 2.6 | 3.0271 | 70
iiia) | SAWRA KUDDU (37x3) | 111 |  | 0 | 4.514 | 5.1707 | 81.4
iv) | MICRO i/c Patikari & Toss (IPP) | 77 |  |  | 45.22 | 44.723
v) | IPP's Power (Phojal, Baner Sangam, Chanju, Suryaakanta, Sandhya, Kashang, Nanti, Bharagarh & Goodwill ) | - | - | - | 4.3159 | 3.3183 | 55 | 60.6115 |  |  | ='Form-1_AnticipatedVsActual_BI'!V19+'Form-1_AnticipatedVsActual_BI'!V24+'Form-1_AnticipatedVsActual_BI'!V30+'Form-1_AnticipatedVsActual_BI'!V36+'Form-1_AnticipatedVsActual_BI'!V42+'Form-1_AnticipatedVsActual_BI'!V49+'Form-1_AnticipatedVsActual_BI'!V55
| Summary:- | [6 empty] | All Figures in LU's |  |  | -10
1 | HPSEBL Generation |  | 36.137 | 21 | EXPORT THROUGH BANKING/SALE |  | At NR Periphery | At HP Periphery |  |  | 36.95
2 | Baspa-II |  | 10.092 |  | HPSEBL Export through IEX+ PXIL | (A)Market Sale through IEX | 0 | 0
3 | Sawra Kuddu + Kashang |  | 7.186
4 | Solar IPP's |  | 1.66 |  |  | (B) Sale through RTM | 3.275 | 3.275
5 | MICRO (IPP ) |  | 44.723 |  |  | IEX DAM Rate Rs. 0 & TAM Rate /kwh
6 | 0 |  | 0 |  |  | (C ) Total (A+B) |  | 3.275
7 | SECI-Solar (LTA PURCHASE) |  | 1.0159 |  |  |  | 0 | 0
8 | Total Central Sector including SOR & GoHP Share in NJPC, B'suil, CH-I, CH-II (HP Periphery) |  | 164.4787
9 | Free Power to HPSEBL from IPPs (Selling under OA) : Malana, Phojal, Baner Sangam, Chanju HEP, Kashang, Suryakanta, Nanti, Sandhaya, Bharagarh & Goodwill(KUT) |  | 3.1228 |  | BRPL THROUGH MPL |  | 0 | 0
10 | Bilateral Share (Shanan+RSD+UP+UK+SAINJ) |  | 13.4161 |  | BYPL THROUGH APPCPL |  | 0 | 0 | x2
11 | Total availability (1 to 4 + 6 to 9) |  | 281.8315 |  | BRPL THROUGH APPCPL |  | 0 | 0
12 | Total GoHP Power as per last revision. |  | 84.0578 |  | PSPCL THROUGH APPCPL & PTC |  | 0 | 0 | [8 empty] | 0
13 | Actual GoHP share sold out side HP to other states FP 12% in Ch-1, Ch-2, B.Suil, FP 13% in Ch3, Parbati-3, 13 % FP in Rampur, FP 12% NJPC & Koldam purchased form GoHP @ Rs.8.43 |  | 42.7733 |  | BYPL THROUGH STATKRAFT |  | 0 | 0 | [5 empty] | 1
14 | GoHP share Schedule to HPSEBL Equity : NJPC 22%, Rampur 26.1%, Koldam 15% UA & SORHPSEBL Purchase from GoHP power () (at HP periphery) |  | 41.221 |  | PUNJAB THROUGH APPCPL |  | 0 | 0
15 | Additional RTM/URS power Purchased GoHP |  | 0.05815 |  | BYPL THROUGH MPL |  | 0 | 0
16 | GoHP Power in/out (+/-) from the Grid |  | 0.063475 |  | AS & WHEN |  | 0 | 0 | [9 empty] | 6.19 | 19.5463
17 | SOR |  | 7.4423 |  | AS & WHEN :-
18 | Malana & other IPP's (selling out side) in/out (+/-) from HPSEBL system |  | 0.13374 |  | WEST BENGAL THROUGH IPCL |  | 0 | 0 | 17 | =((Report_DPS!$I$35*0.8)*0.96)-ABS('Form-1_AnticipatedVsActual_BI'!$L$28)+(('Form-1_AnticipatedVsActual_BI'!$G31*1)*0.9525)-ABS('Form-1_AnticipatedVsActual_BI'!$L31)+(('Form-1_AnticipatedVsActual_BI'!$G32*0.87)*0.96)-ABS('Form-1_AnticipatedVsActual_BI'!$L32)
19 | Net Availability with HPSEBL (10-12+17) |  | 239.0582 |  | MEGHALAYA THROUGH KEIPL |  | 0 | 0
20 | IMPORT THROUGH BANKING/ PURCHASE | At NR Periphery | At HP Periphery |  | WEST BENGAL THROUGH IPCL |  | 0 | 0
| Market Purchase (OA Consumers) | 0 | 0 |  |  |  | 0 | 0 | -152.426
| HPSEBL Import Through IEX @ 3.48 | 31.3248 | 30.2503 |  |  |  | 0 | 0
| Import through RTM IEX | 53.0865 | 51.2657 |  |  |  | 0 | 0
| G DAM THROUGH HPSEBL | 0 | 0 |  |  |  | 0 | 0
| GoHP to HPSEBL | 0 | 0 |  |  |  | 0 | 0 | OD/UD During Min./Max. Frequency
| BRPL through APPCL | 0 | 0 | 22 | Total Export |  | 3.275 | 3.275 | Min. Freq. | Time | O/D | U/D | Max. Freq. | Time | O/D | U/D | Average .Freq.
| BRPL through MPL | 0 | 0 | 23 | Availability after Import/Export (18+20-22) |  |  | 317.2992 | 49.81 | 09.45 | 0 | 35 | 50.26 | 18.15 | 89 | 0 | 50.0092
| BRPL through MPL | 0 | 0 | 24 | Demand of the State |  |  | 319.44
| MEJA | 0 | 0 | 25 | Over/Under drawl(-/+) [23-24] |  |  | -2.1408
| PUNJAB through APPCPL | 0 | 0 | 26 | Tentative UI rate in Rupees (OD & UD), Avg |  |  | 2.5 , 4.59 & -0.48 |  |  |  | G67 | ="Gas:" & IF('Surrendered Energy'!AX105<0,0,ROUND('Surrendered Energy'!AX105,2))&" & Thermal:" &IF('Surrendered Energy'!AY105<0,0,ROUND('Surrendered Energy'!AY105,2))
| IEXL ( JPL-2 & DBPL & OPGPGUNIT1TN) | 0 | 0 | 27 | Load Shedding |  |  | 0 |  |  |  | I67 | =IF(AND('Surrendered Energy'!AY105<0,'Surrendered Energy'!AX105<0),0,IF(AND('Surrendered Energy'!AY105>=0,'Surrendered Energy'!AX105>=0),('Surrendered Energy'!AY105+'Surrendered Energy'!AX105),IF('Surrendered Energy'!AX105>0,'Surrendered Energy'!AX105,'Surrendered Energy'!AY105)))
| BYPL through APPCPL | 0 | 0 | 28 | Unrestricted Demand |  |  | 319.44
|  |  |  | 29 | Average Frequency (Hz) :(Max.Freq. 50.26 at 18.15 Hrs, Min.Freq. 49.81 at 09.45 Hrs) |  |  | 50.0092
|  |  |  | 30 | Max Demand observed (MW) (at 07.30 Hrs.) |  |  | 1662
|  |  |  | 31 | Min Demand at observed (MW) (at 03.45 Hrs.) |  |  | 1027
|  |  |  | 32 | Central Share Surrendered | LF & RF |  | 0
[6 empty] | Gas: 0 & Thermal: 0 |  | 0
21 | Total Import by HPSEBL | 84.4113 | 81.516 |  |  | Total Surrendered :(Amount: 0 Lacs, Avg. Rate: 0) |  | 0
22 | URS Booked |  | 32.2441 |  | INDUSTRIAL CONSUMPTION |  |  | 219.8749
23 | Availability with HP (18-21) |  | 206.8141
* Means no communication. Generation assumed.
** Includes Generation of mini/micro power Houses of HPSEBL.
Copy to:-
| The Chief Engineer (HPSLDC), GoHP, Totu, Shimla-11. | [5 empty] | Shift Incharge
HPSLDC, GoHP, Totu,Shimla-11.
1 | Own | 99.798
2 | Central Sector | 164.4787
3 | Bilateral (Shared+Malana afterExport) | 13.4161
4 | GoHP Power (in/out) | 42.7733
5 | Malana (in/out) | 0.13374
. | OD/UD |  | -2.1408
| Total Gen. | Demand Met | Max Demand Met MW | RE/Green Power Sold (Lus)
| 92.612 | 319.44 | 1662 | 0
Note on D61: ControlRoom:
Note on D63: Malana, Phojal, Baner Sangam, Chanju HEP, Kashang, Suryakanta, Nanti, Sandhaya, Bharagarh & Goodwill(KUT) (in/out)
Note on I74: dba: