## Report_PSPR NRLDC SLDC
File Name: PSPR- |  |  | 2024-04-19
Hiamchal Pradesh State Load Despatch Centre
[18 empty] | DATED | 2024-04-20
FROM | [15 empty] | TO
| POWER CONTROLLER | [16 empty] | D.G.M.,NRLDC,NEW DELHI
| HPSLDC, GoHP, Totu, Shimla-11 | [16 empty] | FAX # 011-26852747-26853082
(FAX #: 0177 2837543)
|  |  | DEMAND AND POWER SUPPLY POSITION | [18 empty] | DEMAND OF STATE |  |  | 30681 | MWh
[22 empty] | ACTUAL MALANA GENERATION |  |  | 581 | MWh
|  | State:- Himachal Pradesh | [19 empty] | ACTUAL BASPA GENERATION |  |  | 999 | MWh | MALANA-II | 492 | MWh |  |  |  |  | SN | Time Block | Frequency | Avg. Freq. | Demand | Avg Demand
[18 empty] | PEAK DEMAND(MW) |  | 1610 | [6 empty] | HOLI BAJOLI | 1775.034 | MWh |  |  |  |  | 1 | 00.00-00.15 | 49.99 |  | 1119
|  | Month/Day :- |  |  |  |  | 2024-04-19 | [10 empty] | Min.DEMAND(MW) |  | 996 |  | ACTUAL OWN GENERATION |  |  | 11251.035 | MWh | SWARA KUDDU | 529 | MWh |  |  |  |  | 2 | 00.15-00.30 | 50.03 |  | 1096
[34 empty] | 3 | 00.30-00.45 | 50.05 |  | 1086 |  | for VLOOKUP(MaxGenHrs.)
HRS. OF THE DAY | GENERATION (MW) | [6 empty] | NET IMPORT (MW) | DEMAND MET (MW) | FREQ-UENCY CORREC-TION (MW) | DEMAND NOT MET | [7 empty] | TOTAL DEMAND NOT MET (MW) | TOTAL ENERGY EQUIVA-LENT TO DEMAND NOT MET (MU) | TOTAL UNRESTRI-CTED DEMAND (MW) P7=P1+P2+P11 | HRS. OF THE DAY | GENERATION (MW) |  |  |  | AVERAGE DEMAND MET (MW) | MAX DEMAND (HOURLY) | MIN DEMAND (HOURLY) | DEMAND ADJUSTMENT(MAXIMUM/MINIMUM/AVERAGE) | CALCULATION MAX/MIN ACTUAL | DEMAND TREND | DUE TO LOAD SHEDD-ING (MW) | 4 | 00.45-01.00 | 50.07 | 50.035 | 1083 | 1096 | Malana | HRS. OF THE DAY | TIME | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | TOTAL
[11 empty] | Low Availability (in MW) | Financial Constraints (in MW) | Emergency load shedding due to security and reliability of the Grid-over Drawl (in MW) | Planned maintenance in transmission system (in MW) | Distribution constraints (in MW) | Planned maintenance in distribution system (in MW) | Tranmission constraints | Any other reasion ( to be specfied) (MW) | [15 empty] | 5 | 01.00-01.15 | 50.03 |  | 1062 |  |  |  | MALANA-2 | 21 | 21 | 21 | 21 | 25.5 | 96.75 | 99 | 98.25 | 2.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.75 | 15 | 14 | 14 | 14 | 14 | 489.5
[34 empty] | 6 | 01.15-01.30 | 50.04 |  | 1061 |  |  |  | SWARA KUDDU | 1.5 | 0 | 0 | 0 | 0 | 0 | 19 | 38.25 | 81 | 61 | 37 | 18.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 37 | 37 | 37.5 | 80.5 | 81 | 530
[34 empty] | 7 | 01.30-01.45 | 50.01 |  | 1061
[34 empty] | 8 | 01.45-02:00 | 50.03 | 50.0275 | 1046 | 1057.5
| OWN GEN | Malana | BASPA | MALANA-II | SAWRA KUDDU | BAJOLI HOLI | TOTAL | [15 empty] | OWN Generation | Malana | BASPA | TOTAL | [7 empty] | 9 | 02.00-02.15 | 50.01 |  | 1038 |  | Malana
[9 empty] | 5+6 | [24 empty] | 10 | 02.15-02.30 | 50.01 |  | 1065
[9 empty] | P1 | P2 | P3 | P4 | P5 | P6 | P7 | P8 | P9 | P10 | P11 | P11/1000 | P12 | [5 empty] | P1 | [5 empty] | P3 | 11 | 02.30-02.45 | 49.99 |  | 1053
1 | 2 | 3 | 4 | 5 | 6 |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 7 | 8 | 9 | 10 | 12 | 02.45-03:00 | 50.01 | 50.005 | 1027 | 1045.75
1 | 595.7477 | 44.2093 | 217.8899 | 21 | 1.5 | 94 | 974.3469 | 122.6542 | 1097.0011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1097.0011 | 1 | 605.4583 | 44 | 215 | 864.4583 | 1096 | 1119 | 1083 | 1096 | 1096 | 1097.0011 | 0 | 13 | 03.00-03.15 | 49.97 |  | 1021 |  | 44 | 1
2 | 504.9773 | 44.2093 | 191.2871 | 21 | 0 | 93.25 | 854.7236 | 203.7423 | 1058.466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1058.466 | 2 | 513.2083 | 44 | 188.75 | 745.9583 | 1057.5 | 1062 | 1046 | 1057.5 | 1057.5 | 1058.466 | 0 | 14 | 03.15-03.30 | 50 |  | 1005 |  | 44 | 2
3 | 475.0895 | 32.1522 | 32.9369 | 21 | 0 | 93 | 654.1785 | 392.5268 | 1046.7052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1046.7052 | 3 | 482.8333 | 32 | 32.5 | 547.3333 | 1045.75 | 1065 | 1027 | 1045.75 | 1045.75 | 1046.7052 | 0 | 15 | 03.30-03.45 | 50.04 |  | 997 |  | 32 | 3
4 | 437.8219 | 32.1522 | 0 | 21 | 0 | 63.5 | 554.4741 | 452.4448 | 1006.9189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1006.9189 | 4 | 444.9583 | 32 | 0 | 476.9583 | 1006 | 1021 | 997 | 1006 | 1006 | 1006.9189 | 0 | 16 | 03.45-04.00 | 50.02 | 50.0075 | 1001 | 1006 | 32 | 4
5 | 410.9844 | 32.1522 | 0 | 25.5 | 0 | 64 | 532.6365 | 413.3635 | 946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 50 | 0.05 | 996 | 5 | 417.6833 | 32 | 0 | 449.6833 | 986.25 | 1021 | 946 | 946 | 946 | 946 | 50 | 17 | 04.00-04.15 | 50.01 |  | 1015 |  | 32 | 5
6 | 419.9138 | 44.2093 | 0.25336 | 96.75 | 0 | 64 | 625.1264 | 450.1049 | 1075.2313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 50 | 0.05 | 1125.2313 | 6 | 426.7583 | 44 | 0.25 | 471.0083 | 1074.25 | 1224 | 962 | 1074.25 | 1074.25 | 1075.2313 | 50 | 18 | 04.15-04.30 | 50.01 |  | 1021 |  | 44 | 6
7 | 583.9894 | 44.2093 | 90.1963 | 99 | 19 | 82.25 | 918.645 | 546.6923 | 1465.3373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1465.3373 | 7 | 593.5083 | 44 | 89 | 726.5083 | 1464 | 1555 | 1353 | 1464 | 1464 | 1465.3373 | 0 | 19 | 04.30-04.45 | 49.99 |  | 946 |  | 44 | 7
8 | 559.5626 | 44.2093 | 73.4745 | 98.25 | 38.25 | 60 | 873.7463 | 736.2537 | 1610 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1610 | 8 | 568.6833 | 44 | 72.5 | 685.1833 | 1597.75 | 1610 | 1587 | 1610 | 1610 | 1610 | 0 | 20 | 04.45-05.00 | 50 | 50.0025 | 963 | 986.25 | 44 | 8
9 | 471.5718 | 28.8867 | 23.8159 | 2.25 | 81 | 59 | 666.5244 | 878.3855 | 1544.9099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1544.9099 | 9 | 479.2583 | 28.75 | 23.5 | 531.5083 | 1543.5 | 1560 | 1525 | 1543.5 | 1543.5 | 1544.9099 | 0 | 21 | 05.00-05.15 | 49.99 |  | 962 |  | 28.75 | 9
10 | 449.3835 | 0.25119 | 0 | 0 | 61 | 60 | 570.6346 | 957.51 | 1528.1446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0.002 | 1530.1446 | 10 | 456.7083 | 0.25 | 0 | 456.9583 | 1526.75 | 1553 | 1513 | 1526.75 | 1526.75 | 1528.1446 | 2 | 22 | 05.15-05.30 | 49.99 |  | 1027 |  | 0.25 | 10
11 | 437.0839 | 0 | 0 | 0 | 37 | 61 | 535.0839 | 992.5602 | 1527.6442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.875 | 0 | 1.875 | 0.001875 | 1529.5192 | 11 | 444.2083 | 0 | 0 | 444.2083 | 1526.25 | 1548 | 1508 | 1526.25 | 1526.25 | 1527.6442 | 1.875 | 23 | 05.30-05.45 | 49.99 |  | 1084 |  | 0 | 11
12 | 433.3941 | 0 | 0 | 0 | 18.75 | 63.75 | 515.8941 | 1011.4998 | 1527.3939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1527.3939 | 12 | 440.4583 | 0 | 0 | 440.4583 | 1526 | 1552 | 1507 | 1526 | 1526 | 1527.3939 | 0 | 24 | 05.45-06.00 | 50.02 | 49.9975 | 1224 | 1074.25 | 0 | 12
13 | 410.271 | 0 | 0 | 0 | 0 | 61 | 471.271 | 979.3028 | 1450.5738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1450.5738 | 13 | 416.9583 | 0 | 0 | 416.9583 | 1449.25 | 1480 | 1359 | 1449.25 | 1449.25 | 1450.5738 | 0 | 25 | 06.00-06.15 | 50.04 |  | 1353 |  | 0 | 13
14 | 370.8141 | 0 | 0 | 0 | 0 | 56.5 | 427.3141 | 940.1839 | 1367.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1367.498 | 14 | 376.8583 | 0 | 0 | 376.8583 | 1366.25 | 1380 | 1368 | 1366.25 | 1366.25 | 1367.498 | 0 | 26 | 06.15-06.30 | 50.03 |  | 1446 |  | 0 | 14
15 | 485.2243 | 0 | 0 | 0 | 0 | 58.5 | 543.7243 | 909.8523 | 1453.5766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1453.5766 | 15 | 493.1333 | 0 | 0 | 493.1333 | 1452.25 | 1468 | 1434 | 1452.25 | 1452.25 | 1453.5766 | 0 | 27 | 06.30-06.45 | 50.08 |  | 1502 |  | 0 | 15
16 | 506.527 | 0 | 0 | 0 | 0 | 59 | 565.527 | 871.2842 | 1436.8113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1436.8113 | 16 | 514.7833 | 0 | 0 | 514.7833 | 1435.5 | 1454 | 1425 | 1435.5 | 1435.5 | 1436.8113 | 0 | 28 | 06.45-07.00 | 50.1 | 50.0625 | 1555 | 1464 | 0 | 16
17 | 379.3746 | 0 | 0 | 0 | 0 | 47 | 426.3746 | 899.5855 | 1325.9601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.9167 | 0 | 21.9167 | 0.021917 | 1347.8768 | 17 | 385.5583 | 0 | 0 | 385.5583 | 1324.75 | 1396 | 1286 | 1324.75 | 1324.75 | 1325.9601 | 21.9167 | 29 | 07.00-07.15 | 50.1 |  | 1604 |  | 0 | 17
18 | 412.0913 | 0.25119 | 26.8562 | 0 | 0 | 38.5 | 477.6987 | 809.9765 | 1287.6752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6 | 0 | 8.6 | 0.0086 | 1296.2752 | 18 | 418.8083 | 0.25 | 26.5 | 445.5583 | 1286.5 | 1299 | 1270 | 1286.5 | 1286.5 | 1287.6752 | 8.6 | 30 | 07.15-07.30 | 50.04 |  | 1610 |  | 0.25 | 18
19 | 442.5941 | 13.8154 | 40.2843 | 12.75 | 0.5 | 96.75 | 606.6938 | 668.9704 | 1275.6642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.6642 | 19 | 449.8083 | 13.75 | 39.75 | 503.3083 | 1274.5 | 1290 | 1247 | 1274.5 | 1274.5 | 1275.6642 | 0 | 31 | 07.30-07.45 | 50.06 |  | 1590 |  | 13.75 | 19
20 | 431.0326 | 43.4557 | 50.4187 | 15 | 37 | 97 | 673.907 | 545.7061 | 1219.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 46 | 0.046 | 1265.613 | 20 | 438.0583 | 43.25 | 49.75 | 531.0583 | 1218.5 | 1280 | 1109 | 1218.5 | 1218.5 | 1219.613 | 46 | 32 | 07.45-08.00 | 50.06 | 50.065 | 1587 | 1597.75 | 43.25 | 20
21 | 447.0219 | 44.2093 | 34.7104 | 14 | 37 | 96.5 | 673.4416 | 516.8947 | 1190.3363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1190.3363 | 21 | 454.3083 | 44 | 34.25 | 532.5583 | 1189.25 | 1221 | 1162 | 1189.25 | 1189.25 | 1190.3363 | 0 | 33 | 08.00-08.15 | 50.04 |  | 1555 |  | 44 | 21
22 | 526.2309 | 44.2093 | 62.8334 | 14 | 37.5 | 96 | 780.7735 | 352.761 | 1133.5345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1133.5345 | 22 | 534.8083 | 44 | 62 | 640.8083 | 1132.5 | 1183 | 1101 | 1132.5 | 1132.5 | 1133.5345 | 0 | 34 | 08.15-08.30 | 50.05 |  | 1525 |  | 44 | 22
23 | 536.5625 | 44.2093 | 52.9523 | 14 | 80.5 | 101.5 | 829.724 | 234.4972 | 1064.2212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 0 | 5.5 | 0.0055 | 1069.7212 | 23 | 545.3083 | 44 | 52.25 | 641.5583 | 1063.25 | 1071 | 1059 | 1063.25 | 1063.25 | 1064.2212 | 5.5 | 35 | 08.30-08.45 | 50.05 |  | 1560 |  | 44 | 23
24 | 523.771 | 44.2093 | 101.0908 | 14 | 81 | 105.5 | 869.571 | 169.8776 | 1039.4486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1039.4486 | 24 | 532.3083 | 44 | 99.75 | 676.0583 | 1038.5 | 1045 | 1029 | 1038.5 | 1038.5 | 1039.4486 | 0 | 36 | 08.45-09.00 | 50.08 | 50.055 | 1534 | 1543.5 | 44 | 24
[34 empty] | 37 | 09.00-09.15 | 50.1 |  | 1553
TOTAL (in MWh) | 11251.035 | 581 | 999 | 489.5 | 530 | 1771.5 | 15622.035 | 15056.6302 | 30678.6652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185.8917 | 0 | 185.8917 | 0.18589 | 30864.5569 | TOTAL | 11434.425 | 578.25 | 985.75 | 12998.425 | 30681 |  |  | 30653 | 30653 | 30678.6652 | 185.8917 | 38 | 09.15-09.30 | 50.05 |  | 1516
[34 empty] | 39 | 09.30-09.45 | 50.03 |  | 1525
[34 empty] | 40 | 09.45-10.00 | 50.06 | 50.06 | 1513 | 1526.75
|  |  | Hourly Average Frequency (Fr) |  |  |  | 5+6 P4 12: 50.0155; 5+6 P6 14: HZ | Note :- Please don't edit these figures. | [11 empty] | 41 | 10.00-10.15 | 50.04 |  | 1517
|  |  | Demand met for the day |  |  |  | 5+6 P4 12: 1610; 5+6 P6 14: MW | [12 empty] | 42 | 10.15-10.30 | 50.04 |  | 1508
|  |  | Unrestricted Demand for the day |  |  |  | 5+6 P4 12: 1610; 5+6 P6 14: MW | MAX = | 1610 | [10 empty] | 43 | 10.30-10.45 | 50.01 |  | 1548
|  |  | Minimum Demand(Unrestricted) for the day |  |  |  | 5+6 P4 12: 996; 5+6 P6 14: MW; 5+6 P11 19: Aux.; 5+6 P11/1000 20: Net gen. | MIN = | 946 | [10 empty] | 44 | 10.45-11.00 | 50.02 | 50.0275 | 1532 | 1526.25
|  |  | Gross own generation |  |  |  | 5+6 P4 12: 11251.035; 5+6 P6 14: MWH; 5+6 P11 19: 23.51; 5+6 P11/1000 20: 11227.525 | [12 empty] | 45 | 11.00-11.15 | 50.05 |  | 1535
|  |  | Gross Baspa generation |  |  |  | 5+6 P4 12: 999; 5+6 P6 14: MWH; 5+6 P11 19: 1.98; 5+6 P11/1000 20: 997.02 | [12 empty] | 46 | 11.15-11.30 | 50 |  | 1552
|  |  | Gross Malana generation |  |  |  | 5+6 P4 12: 581; 5+6 P6 14: MWH; 5+6 P11 19: 1.65; 5+6 P11/1000 20: 579.35 | [12 empty] | 47 | 11.30-11.45 | 49.99 |  | 1510
|  |  | Malana generation at 0300 Hrs. |  |  |  | 5+6 P4 12: 32; 5+6 P6 14: MW | [12 empty] | 48 | 11.45-12.00 | 50 | 50.01 | 1507 | 1526
|  |  | Malana generation at 2400 Hrs. |  |  |  | 5+6 P4 12: 44; 5+6 P6 14: MW | [12 empty] | 49 | 12.00-12.15 | 50.03 |  | 1480
|  |  | Max.generation of Malana at 100 Hrs. |  |  |  | 5+6 P4 12: 44; 5+6 P6 14: MW | [12 empty] | 50 | 12.15-12.30 | 50.05 |  | 1459
[7 empty] | 5+6 P2 10: Off Peak Hrs MW; 5+6 P4 12: Peak Hrs MW; 5+6 P11 19: Gross Lus; 5+6 P11/1000 20: Net Lus | [14 empty] | 50.04 |  | 1444
|  |  | Total Own Generation |  |  |  | 5+6 P2 10: 486.7497; 5+6 P4 12: 395.0464; 5+6 P11 19: 112.5104; 5+6 P11/1000 20: 112.2752 | [12 empty] | 51 | 12.30-12.45 | 50.08 | 50.05 | 1414 | 1449.25
|  |  | Above 25 MW |  |  |  | 5+6 P2 10: 108.3508; 5+6 P4 12: 75.3296; 5+6 P11 19: 27.067; 5+6 P11/1000 20: 26.8803 | [12 empty] | 52 | 12.45-13.00 | 50.28 |  | 1359
|  |  | Below 25 MW(Small Hydro <25 MW) |  |  |  | 5+6 P2 10: 378.399; 5+6 P4 12: 319.7168; 5+6 P11 19: 85.4433; 5+6 P11/1000 20: 85.395 | [12 empty] | 53 | 13.00-13.15 | 50.26 |  | 1358
[34 empty] | 55 | 13.30-13.45 | 50.12 |  | 1368
[34 empty] | 56 | 13.45-14.00 | 50 | 50.165 | 1380 | 1366.25
[7 empty] | 5+6 P11 19: Shift Incharge | [12 empty] | 57 | 14.00-14.15 | 49.93 |  | 1434
[7 empty] | 5+6 P11 19: HPSLDC, GoHP, Totu,Shimla-11. | [12 empty] | 58 | 14.15-14.30 | 49.88 |  | 1440
Load Shedding For Dated | [6 empty] | 5+6 P1 9: 2024-04-19 | [12 empty] | 59 | 14.30-14.45 | 49.95 |  | 1468
[34 empty] | 60 | 14.45-15.00 | 49.99 | 49.9375 | 1467 | 1452.25 | bar: 7 to 5+6 P4 12; 5+6 P12 21
SR.NO. | NAME OF FEEDER / SubStation | LOAD IN MW |  |  | TIME PERIOD |  | 5+6 P1 9: DURATION; 5+6 P3 11: LOAD SHEDDING IN LUS; 5+6 P4 12: REASON | [12 empty] | 61 | 15.00-15.15 | 50.01 |  | 1454
|  | BEFORE SHEDD-ING | AFTER SHEDD-ING | LOAD SHEDD-ING | FROM | [28 empty] | 62 | 15.15-15.30 | 50.02 |  | 1438 | bar: 7 to 5+6 P4 12; 5+6 P12 21
[5 empty] | Hour | Minute | 7: Hour; 8: Minute; 5+6 P1 9: Hour; 5+6 P2 10: Minute | [12 empty] | 63 | 15.30-15.45 | 49.98 |  | 1425
1 | 2 | 3 | 4 | 5 | 6 | 7 | 7: 8; 8: 9; 5+6 P1 9: 10; 5+6 P2 10: 11; 5+6 P3 11: 12; 5+6 P4 12: 13 | [12 empty] | 64 | 15.45-16.00 | 49.94 | 49.9875 | 1425 | 1435.5
1 | 220 KV UPNGL- Kinwin line | 2.5 | 0 | 2.5 | 9 | 12 | 7: 10; 8: 45; 5+6 P1 9: 1; 5+6 P2 10: 33; 5+6 P3 11: 0.03875; 5+6 P4 12: Emergency shutdown for jumper repair. | [12 empty] | 65 | 16.00-16.15 | 50.02 |  | 1396
2 | 220k Uperla Nangal-Nalagarh ckt-1 & 2 | 100 | 0 | 100 | 4 | 30 | 7: 5; 8: 30; 5+6 P1 9: 1; 5+6 P2 10: 0; 5+6 P3 11: 1; 5+6 P4 12: O/C earth fault R phase | [12 empty] | 66 | 16.15-16.30 | 49.97 |  | 1315
3 | 132KV Amb Gagret line | 48 | 0 | 48 | 16 | 17 | 7: 16; 8: 27; 5+6 P1 9: 0; 5+6 P2 10: 10; 5+6 P3 11: 0.08; 5+6 P4 12: O/C earth fault R phase | [12 empty] | 67 | 16.30-16.45 | 49.96 |  | 1302
4 | 132 KV Kangra PSEB line | 11 | 0 | 11 | 16 | 15 | 7: 17; 8: 5; 5+6 P1 9: 0; 5+6 P2 10: 50; 5+6 P3 11: 0.091667; 5+6 P4 12: O/C earth fault | [12 empty] | 68 | 16.45-17.00 | 50 | 49.9875 | 1286 | 1324.75
5 | 132 KV Kangra Dehra line | 17 | 0 | 17 | 16 | 48 | 7: 17; 8: 13; 5+6 P1 9: 0; 5+6 P2 10: 25; 5+6 P3 11: 0.070833; 5+6 P4 12: O/C earth fault B phase | [12 empty] | 69 | 17.00-17.15 | 50.01 |  | 1280
6 | 132 KV Hamirpur Dehra line | 8 | 0 | 8 | 16 | 43 | 7: 17; 8: 6; 5+6 P1 9: 0; 5+6 P2 10: 23; 5+6 P3 11: 0.030667; 5+6 P4 12: O/C earth fault B phase | [12 empty] | 70 | 17.15-17.30 | 49.92 |  | 1299
7 | 66 KV Totu Parwanoo line | 5 | 0 | 5 | 17 | 5 | 7: 17; 8: 17; 5+6 P1 9: 0; 5+6 P2 10: 12; 5+6 P3 11: 0.01; 5+6 P4 12: E/F R phase | [12 empty] | 71 | 17.30-17.45 | 49.94 |  | 1297
8 | 132 KV Bassi Palampur line | 22 | 0 | 22 | 17 | 25 | 7: 17; 8: 31; 5+6 P1 9: 0; 5+6 P2 10: 6; 5+6 P3 11: 0.022; 5+6 P4 12: E/F R,Y,B phase | [12 empty] | 72 | 17.45-18.00 | 49.93 | 49.95 | 1270 | 1286.5
[34 empty] | 73 | 18.00-18.15 | 49.95 |  | 1289 | bar: 5+6 P12 21
[34 empty] | 74 | 18.15-18.30 | 49.99 |  | 1290 | bar: 5+6 P12 21
[34 empty] | 75 | 18.30-18.45 | 49.99 |  | 1272 | bar: 5+6 P12 21
[34 empty] | 76 | 18.45-19.00 | 49.96 | 49.9725 | 1247 | 1274.5 | bar: 5+6 P12 21
[34 empty] | 77 | 19.00-19.15 | 49.94 |  | 1270 | bar: 5+6 P12 21
[34 empty] | 78 | 19.15-19.30 | 49.91 |  | 1280 | bar: 5+6 P12 21
[34 empty] | 79 | 19.30-19.45 | 49.97 |  | 1215 | bar: 5+6 P12 21
[34 empty] | 80 | 19.45-20.00 | 49.99 | 49.9525 | 1109 | 1218.5 | bar: 5+6 P12 21
[34 empty] | 81 | 20.00-20.15 | 50 |  | 1221 | bar: 5+6 P12 21
[34 empty] | 82 | 20.15-20.30 | 49.98 |  | 1201 | bar: 5+6 P12 21
[34 empty] | 83 | 20.30-20.45 | 49.86 |  | 1162 | bar: 5+6 P12 21
[34 empty] | 84 | 20.45-21.00 | 49.95 | 49.9475 | 1173 | 1189.25 | bar: 5+6 P12 21
[34 empty] | 85 | 21.00-21.15 | 49.98 |  | 1183 | bar: 5+6 P12 21
[34 empty] | 86 | 21.15-21.30 | 50.04 |  | 1134 | bar: 5+6 P12 21
[34 empty] | 87 | 21.30-21.45 | 50.04 |  | 1112
[34 empty] | 88 | 21.45-22.00 | 50.06 | 50.03 | 1101 | 1132.5
[34 empty] | 89 | 22.00-22.15 | 50.04 |  | 1071
[34 empty] | 90 | 22.15-22.30 | 50.02 |  | 1061
[34 empty] | 91 | 22.30-22.45 | 50.01 |  | 1062
[34 empty] | 92 | 22.45-23.00 | 49.99 | 50.015 | 1059 | 1063.25
[34 empty] | 93 | 23.00-23.15 | 50 |  | 1045
[34 empty] | 94 | 23.15-23.30 | 50.01 |  | 1036
[34 empty] | 95 | 23.30-23.45 | 50.03 |  | 1044
[34 empty] | 96 | 23.45-24.00 | 50.05 | 50.0225 | 1029 | 1038.5
[35 empty] | Total | 50.0155 | 50.0155 | 30681 | 30681
[35 empty] | max | 1610 |  | avg. max | 1597.75
[35 empty] | min | 946 |  | avg. min | 986.25
Note on AG16: ReportServer: critical formulas…….do not disturb
Note on AH16: ReportServer: critical formulas…….do not disturb
Note on Y24: Please don't edit here
Note on H25: Column no. 5 =Sum (2+3+4 Column)
Note on L25: The fig of power cut comes from daily hourly load sheet.