## Report_PSPR NRLDC SLDC
File Name: PSPR- |  |  | 2024-04-21
Hiamchal Pradesh State Load Despatch Centre
[18 empty] | DATED | 2024-04-22
FROM | [15 empty] | TO
| POWER CONTROLLER | [16 empty] | D.G.M.,NRLDC,NEW DELHI
| HPSLDC, GoHP, Totu, Shimla-11 | [16 empty] | FAX # 011-26852747-26853082
(FAX #: 0177 2837543)
|  |  | DEMAND AND POWER SUPPLY POSITION | [18 empty] | DEMAND OF STATE |  |  | 29384 | MWh
[22 empty] | ACTUAL MALANA GENERATION |  |  | 530 | MWh
|  | State:- Himachal Pradesh | [19 empty] | ACTUAL BASPA GENERATION |  |  | 1149 | MWh | MALANA-II | 545 | MWh |  |  |  |  | SN | Time Block | Frequency | Avg. Freq. | Demand | Avg Demand
[18 empty] | PEAK DEMAND(MW) |  | 1501 | [6 empty] | HOLI BAJOLI | 1791.756 | MWh |  |  |  |  | 1 | 00.00-00.15 | 50 |  | 1108
|  | Month/Day :- |  |  |  |  | 2024-04-21 | [10 empty] | Min.DEMAND(MW) |  | 1002 |  | ACTUAL OWN GENERATION |  |  | 11268.28 | MWh | SWARA KUDDU | 530 | MWh |  |  |  |  | 2 | 00.15-00.30 | 50.01 |  | 1095
[34 empty] | 3 | 00.30-00.45 | 50.01 |  | 1074 |  | for VLOOKUP(MaxGenHrs.)
HRS. OF THE DAY | GENERATION (MW) | [6 empty] | NET IMPORT (MW) | DEMAND MET (MW) | FREQ-UENCY CORREC-TION (MW) | DEMAND NOT MET | [7 empty] | TOTAL DEMAND NOT MET (MW) | TOTAL ENERGY EQUIVA-LENT TO DEMAND NOT MET (MU) | TOTAL UNRESTRI-CTED DEMAND (MW) P7=P1+P2+P11 | HRS. OF THE DAY | GENERATION (MW) |  |  |  | AVERAGE DEMAND MET (MW) | MAX DEMAND (HOURLY) | MIN DEMAND (HOURLY) | DEMAND ADJUSTMENT(MAXIMUM/MINIMUM/AVERAGE) | CALCULATION MAX/MIN ACTUAL | DEMAND TREND | DUE TO LOAD SHEDD-ING (MW) | 4 | 00.45-01.00 | 50.03 | 50.0125 | 1072 | 1087.25 | Malana | HRS. OF THE DAY | TIME | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | TOTAL
[11 empty] | Low Availability (in MW) | Financial Constraints (in MW) | Emergency load shedding due to security and reliability of the Grid-over Drawl (in MW) | Planned maintenance in transmission system (in MW) | Distribution constraints (in MW) | Planned maintenance in distribution system (in MW) | Tranmission constraints | Any other reasion ( to be specfied) (MW) | [15 empty] | 5 | 01.00-01.15 | 50.01 |  | 1063 |  |  |  | MALANA-2 | 30 | 30 | 30 | 30 | 29.75 | 96.5 | 99.5 | 99.75 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.25 | 15 | 15 | 15 | 15 | 15 | 562.75
[34 empty] | 6 | 01.15-01.30 | 50.02 |  | 1054 |  |  |  | SWARA KUDDU | 37.5 | 0.25 | 0 | 0 | 0 | 0 | 0 | 19.5 | 81 | 59.5 | 37 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.5 | 37.75 | 74 | 81 | 81 | 529
[34 empty] | 7 | 01.30-01.45 | 49.98 |  | 1055
[34 empty] | 8 | 01.45-02:00 | 49.94 | 49.9875 | 1041 | 1053.25
| OWN GEN | Malana | BASPA | MALANA-II | SAWRA KUDDU | BAJOLI HOLI | TOTAL | [15 empty] | OWN Generation | Malana | BASPA | TOTAL | [7 empty] | 9 | 02.00-02.15 | 49.92 |  | 1036 |  | Malana
[9 empty] | 5+6 | [24 empty] | 10 | 02.15-02.30 | 49.91 |  | 1032
[9 empty] | P1 | P2 | P3 | P4 | P5 | P6 | P7 | P8 | P9 | P10 | P11 | P11/1000 | P12 | [5 empty] | P1 | [5 empty] | P3 | 11 | 02.30-02.45 | 49.96 |  | 1040
1 | 2 | 3 | 4 | 5 | 6 |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 7 | 8 | 9 | 10 | 12 | 02.45-03:00 | 50 | 49.9475 | 1044 | 1038
1 | 581.6125 | 43.2452 | 219.4862 | 30 | 37.5 | 94 | 1005.8439 | 81.6096 | 1087.4535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1087.4535 | 1 | 592.8333 | 44 | 216 | 852.8333 | 1087.25 | 1108 | 1072 | 1087.25 | 1087.25 | 1087.4535 | 0 | 13 | 03.00-03.15 | 49.98 |  | 1027 |  | 44 | 1
2 | 476.1472 | 42.9995 | 169.9494 | 30 | 0.25 | 86.75 | 806.0961 | 247.3511 | 1053.4472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1053.4472 | 2 | 485.3333 | 43.75 | 167.25 | 696.3333 | 1053.25 | 1063 | 1041 | 1053.25 | 1053.25 | 1053.4472 | 0 | 14 | 03.15-03.30 | 50 |  | 1041 |  | 43.75 | 2
3 | 418.3865 | 19.6569 | 5.0807 | 30 | 0 | 63.25 | 536.3742 | 501.8201 | 1038.1943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1038.1943 | 3 | 426.4583 | 20 | 5 | 451.4583 | 1038 | 1044 | 1032 | 1038 | 1038 | 1038.1943 | 0 | 15 | 03.30-03.45 | 49.98 |  | 1050 |  | 20 | 3
4 | 445.7339 | 19.6569 | 0 | 30 | 0 | 63 | 558.3909 | 481.8038 | 1040.1947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1040.1947 | 4 | 454.3333 | 20 | 0 | 474.3333 | 1040 | 1050 | 1027 | 1040 | 1040 | 1040.1947 | 0 | 16 | 03.45-04.00 | 49.99 | 49.9875 | 1042 | 1040 | 20 | 4
5 | 455.5201 | 19.6569 | 2.2863 | 29.75 | 0 | 63 | 570.2134 | 503.2375 | 1073.4509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1073.4509 | 5 | 464.3083 | 20 | 2.25 | 486.5583 | 1073.25 | 1097 | 1048 | 1073.25 | 1073.25 | 1073.4509 | 0 | 17 | 04.00-04.15 | 49.99 |  | 1048 |  | 20 | 5
6 | 519.854 | 42.5081 | 103.6463 | 96.5 | 0 | 63 | 825.5083 | 387.7188 | 1213.2271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1213.2271 | 6 | 529.8833 | 43.25 | 102 | 675.1333 | 1213 | 1313 | 1119 | 1213 | 1213 | 1213.2271 | 0 | 18 | 04.15-04.30 | 49.97 |  | 1064 |  | 43.25 | 6
7 | 577.9825 | 43.2452 | 110.2512 | 99.5 | 0 | 62 | 892.9789 | 542.2897 | 1435.2686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1435.2686 | 7 | 589.1333 | 44 | 108.5 | 741.6333 | 1435 | 1474 | 1390 | 1435 | 1435 | 1435.2686 | 0 | 19 | 04.30-04.45 | 49.97 |  | 1084 |  | 44 | 7
8 | 519.0446 | 43.2452 | 7.113 | 99.75 | 19.5 | 62 | 750.6528 | 750.3472 | 1501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1501 | 8 | 529.0583 | 44 | 7 | 580.0583 | 1491.75 | 1501 | 1487 | 1501 | 1501 | 1501 | 0 | 20 | 04.45-05.00 | 49.94 | 49.9675 | 1097 | 1073.25 | 44 | 8
9 | 464.1781 | 32.4339 | 0 | 27 | 81 | 59 | 663.612 | 820.6658 | 1484.2778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1484.2778 | 9 | 473.1333 | 33 | 0 | 506.1333 | 1484 | 1494 | 1470 | 1484 | 1484 | 1484.2778 | 0 | 21 | 05.00-05.15 | 49.94 |  | 1119 |  | 33 | 9
10 | 470.2608 | 7.3713 | 0 | 0 | 59.5 | 60 | 597.1321 | 870.6426 | 1467.7747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1467.7747 | 10 | 479.3333 | 7.5 | 0 | 486.8333 | 1467.5 | 1475 | 1456 | 1467.5 | 1467.5 | 1467.7747 | 0 | 22 | 05.15-05.30 | 49.94 |  | 1183 |  | 7.5 | 10
11 | 458.4879 | 0 | 0 | 0 | 37 | 90 | 585.4879 | 857.0321 | 1442.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1442.52 | 11 | 467.3333 | 0 | 0 | 467.3333 | 1442.25 | 1456 | 1435 | 1442.25 | 1442.25 | 1442.52 | 0 | 23 | 05.30-05.45 | 49.96 |  | 1237 |  | 0 | 11
12 | 422.4335 | 0 | 0 | 0 | 1 | 88 | 511.4335 | 877.0764 | 1388.5099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1388.5099 | 12 | 430.5833 | 0 | 0 | 430.5833 | 1388.25 | 1413 | 1363 | 1388.25 | 1388.25 | 1388.5099 | 0 | 24 | 05.45-06.00 | 50.01 | 49.9625 | 1313 | 1213 | 0 | 12
13 | 409.9248 | 0 | 0 | 0 | 0 | 65 | 474.9248 | 830.3195 | 1305.2443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1305.2443 | 13 | 417.8333 | 0 | 0 | 417.8333 | 1305 | 1350 | 1219 | 1305 | 1305 | 1305.2443 | 0 | 25 | 06.00-06.15 | 50.02 |  | 1390 |  | 0 | 13
14 | 392.9032 | 0 | 0 | 0 | 0 | 57 | 449.9032 | 726.317 | 1176.2202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.7333 | 0 | 59.7333 | 0.059733 | 1235.9535 | 14 | 400.4833 | 0 | 0 | 400.4833 | 1176 | 1161 | 1140 | 1176 | 1176 | 1176.2202 | 59.7333 | 26 | 06.15-06.30 | 50.03 |  | 1430 |  | 0 | 14
15 | 427.7558 | 0 | 0 | 0 | 0 | 59.25 | 487.0058 | 683.7133 | 1170.7191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 16 | 0.016 | 1186.7191 | 15 | 436.0083 | 0 | 0 | 436.0083 | 1170.5 | 1202 | 1133 | 1170.5 | 1170.5 | 1170.7191 | 16 | 27 | 06.30-06.45 | 50.02 |  | 1446 |  | 0 | 15
16 | 474.0134 | 0 | 0 | 0 | 0 | 60.25 | 534.2634 | 648.9581 | 1183.2215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1183.2215 | 16 | 483.1583 | 0 | 0 | 483.1583 | 1183 | 1206 | 1168 | 1183 | 1183 | 1183.2215 | 0 | 28 | 06.45-07.00 | 50.03 | 50.025 | 1474 | 1435 | 0 | 16
17 | 492.9235 | 0 | 0 | 0 | 0 | 60 | 552.9235 | 633.2985 | 1186.222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1186.222 | 17 | 502.4333 | 0 | 0 | 502.4333 | 1186 | 1208 | 1164 | 1186 | 1186 | 1186.222 | 0 | 29 | 07.00-07.15 | 50 |  | 1491 |  | 0 | 17
18 | 446.8131 | 0 | 74.9403 | 0 | 0 | 63.75 | 585.5034 | 584.9657 | 1170.4691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1170.4691 | 18 | 455.4333 | 0 | 73.75 | 529.1833 | 1170.25 | 1181 | 1157 | 1170.25 | 1170.25 | 1170.4691 | 0 | 30 | 07.15-07.30 | 50.01 |  | 1487 |  | 0 | 18
19 | 465.2082 | 0.24571 | 42.1698 | 15.25 | 0 | 95.25 | 618.1237 | 550.595 | 1168.7188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1168.7188 | 19 | 474.1833 | 0.25 | 41.5 | 515.9333 | 1168.5 | 1190 | 1156 | 1168.5 | 1168.5 | 1168.7188 | 0 | 31 | 07.30-07.45 | 50.01 |  | 1488 |  | 0.25 | 19
20 | 437.9835 | 42.7538 | 37.0891 | 15 | 19.5 | 96 | 648.3264 | 637.6643 | 1285.9907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1285.9907 | 20 | 446.4333 | 43.5 | 36.5 | 526.4333 | 1285.75 | 1316 | 1219 | 1285.75 | 1285.75 | 1285.9907 | 0 | 32 | 07.45-08.00 | 50.03 | 50.0125 | 1501 | 1491.75 | 43.5 | 20
21 | 435.0403 | 43.2452 | 83.3235 | 15 | 37.75 | 96.25 | 710.609 | 552.1274 | 1262.7364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.7364 | 21 | 443.4333 | 44 | 82 | 569.4333 | 1262.5 | 1288 | 1235 | 1262.5 | 1262.5 | 1262.7364 | 0 | 33 | 08.00-08.15 | 50.01 |  | 1489 |  | 44 | 21
22 | 472.5663 | 43.2452 | 35.0568 | 15 | 74 | 94.25 | 734.1183 | 432.0999 | 1166.2183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1166.2183 | 22 | 481.6833 | 44 | 34.5 | 560.1833 | 1166 | 1206 | 1134 | 1166 | 1166 | 1166.2183 | 0 | 34 | 08.15-08.30 | 50.04 |  | 1470 |  | 44 | 22
23 | 498.3194 | 43.2452 | 45.4723 | 15 | 81 | 94 | 777.0369 | 303.4153 | 1080.4522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1080.4522 | 23 | 507.9333 | 44 | 44.75 | 596.6833 | 1080.25 | 1104 | 1056 | 1080.25 | 1080.25 | 1080.4522 | 0 | 35 | 08.30-08.45 | 50.08 |  | 1494 |  | 44 | 23
24 | 505.1869 | 43.2452 | 213.1353 | 15 | 81 | 93 | 950.5675 | 51.4325 | 1002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1002 | 24 | 514.9333 | 44 | 209.75 | 768.6833 | 1016.75 | 1030 | 1002 | 1002 | 1002 | 1002 | 0 | 36 | 08.45-09.00 | 50.11 | 50.06 | 1483 | 1484 | 44 | 24
[34 empty] | 37 | 09.00-09.15 | 50.03 |  | 1475
TOTAL (in MWh) | 11268.28 | 530 | 1149 | 562.75 | 529 | 1788 | 15827.03 | 13556.5014 | 29383.5314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.7333 | 0 | 75.7333 | 0.075733 | 29459.2647 | TOTAL | 11485.675 | 539.25 | 1130.75 | 13155.675 | 29384 |  |  | 29378.5 | 29378.5 | 29383.5314 | 75.7333 | 38 | 09.15-09.30 | 50.03 |  | 1469
[34 empty] | 39 | 09.30-09.45 | 50 |  | 1470
[34 empty] | 40 | 09.45-10.00 | 49.98 | 50.01 | 1456 | 1467.5
|  |  | Hourly Average Frequency (Fr) |  |  |  | 5+6 P4 12: 49.9871; 5+6 P6 14: HZ | Note :- Please don't edit these figures. | [11 empty] | 41 | 10.00-10.15 | 49.99 |  | 1437
|  |  | Demand met for the day |  |  |  | 5+6 P4 12: 1501; 5+6 P6 14: MW | [12 empty] | 42 | 10.15-10.30 | 49.98 |  | 1456
|  |  | Unrestricted Demand for the day |  |  |  | 5+6 P4 12: 1501; 5+6 P6 14: MW | MAX = | 1501 | [10 empty] | 43 | 10.30-10.45 | 49.95 |  | 1441
|  |  | Minimum Demand(Unrestricted) for the day |  |  |  | 5+6 P4 12: 1002; 5+6 P6 14: MW; 5+6 P11 19: Aux.; 5+6 P11/1000 20: Net gen. | MIN = | 1002 | [10 empty] | 44 | 10.45-11.00 | 49.96 | 49.97 | 1435 | 1442.25
|  |  | Gross own generation |  |  |  | 5+6 P4 12: 11268.28; 5+6 P6 14: MWH; 5+6 P11 19: 62.087; 5+6 P11/1000 20: 11206.193 | [12 empty] | 45 | 11.00-11.15 | 49.98 |  | 1413
|  |  | Gross Baspa generation |  |  |  | 5+6 P4 12: 1149; 5+6 P6 14: MWH; 5+6 P11 19: 1.86; 5+6 P11/1000 20: 1147.14 | [12 empty] | 46 | 11.15-11.30 | 49.96 |  | 1402
|  |  | Gross Malana generation |  |  |  | 5+6 P4 12: 530; 5+6 P6 14: MWH; 5+6 P11 19: 1.4; 5+6 P11/1000 20: 528.6 | [12 empty] | 47 | 11.30-11.45 | 50.02 |  | 1375
|  |  | Malana generation at 0300 Hrs. |  |  |  | 5+6 P4 12: 20; 5+6 P6 14: MW | [12 empty] | 48 | 11.45-12.00 | 49.99 | 49.9875 | 1363 | 1388.25
|  |  | Malana generation at 2400 Hrs. |  |  |  | 5+6 P4 12: 44; 5+6 P6 14: MW | [12 empty] | 49 | 12.00-12.15 | 50 |  | 1350
|  |  | Max.generation of Malana at 100 Hrs. |  |  |  | 5+6 P4 12: 44; 5+6 P6 14: MW | [12 empty] | 50 | 12.15-12.30 | 49.96 |  | 1300
[7 empty] | 5+6 P2 10: Off Peak Hrs MW; 5+6 P4 12: Peak Hrs MW; 5+6 P11 19: Gross Lus; 5+6 P11/1000 20: Net Lus | [14 empty] | 49.92 |  | 1297
|  |  | Total Own Generation |  |  |  | 5+6 P2 10: 434.9497; 5+6 P4 12: 396.6326; 5+6 P11 19: 112.6828; 5+6 P11/1000 20: 112.0619 | [12 empty] | 51 | 12.30-12.45 | 49.97 | 49.9625 | 1273 | 1305
|  |  | Above 25 MW |  |  |  | 5+6 P2 10: 43.9613; 5+6 P4 12: 82.078; 5+6 P11 19: 26.5674; 5+6 P11/1000 20: 25.9904 | [12 empty] | 52 | 12.45-13.00 | 49.96 |  | 1219
|  |  | Below 25 MW(Small Hydro <25 MW) |  |  |  | 5+6 P2 10: 390.9884; 5+6 P4 12: 314.5546; 5+6 P11 19: 86.1155; 5+6 P11/1000 20: 86.0715 | [12 empty] | 53 | 13.00-13.15 | 49.97 |  | 1184
[34 empty] | 55 | 13.30-13.45 | 49.96 |  | 1161
[34 empty] | 56 | 13.45-14.00 | 49.99 | 49.97 | 1140 | 1176
[7 empty] | 5+6 P11 19: Shift Incharge | [12 empty] | 57 | 14.00-14.15 | 49.99 |  | 1133
[7 empty] | 5+6 P11 19: HPSLDC, GoHP, Totu,Shimla-11. | [12 empty] | 58 | 14.15-14.30 | 49.98 |  | 1161
Load Shedding For Dated | [6 empty] | 5+6 P1 9: 2024-04-21 | [12 empty] | 59 | 14.30-14.45 | 49.94 |  | 1186
[34 empty] | 60 | 14.45-15.00 | 49.92 | 49.9575 | 1202 | 1170.5 | bar: 7 to 5+6 P4 12; 5+6 P12 21
SR.NO. | NAME OF FEEDER / SubStation | LOAD IN MW |  |  | TIME PERIOD |  | 5+6 P1 9: DURATION; 5+6 P3 11: LOAD SHEDDING IN LUS; 5+6 P4 12: REASON | [12 empty] | 61 | 15.00-15.15 | 49.9 |  | 1182
|  | BEFORE SHEDD-ING | AFTER SHEDD-ING | LOAD SHEDD-ING | FROM | [28 empty] | 62 | 15.15-15.30 | 49.95 |  | 1168 | bar: 7 to 5+6 P4 12; 5+6 P12 21
[5 empty] | Hour | Minute | 7: Hour; 8: Minute; 5+6 P1 9: Hour; 5+6 P2 10: Minute | [12 empty] | 63 | 15.30-15.45 | 49.97 |  | 1176
1 | 2 | 3 | 4 | 5 | 6 | 7 | 7: 8; 8: 9; 5+6 P1 9: 10; 5+6 P2 10: 11; 5+6 P3 11: 12; 5+6 P4 12: 13 | [12 empty] | 64 | 15.45-16.00 | 50.01 | 49.9575 | 1206 | 1183
1 | 66 KV UPNGL Akanwali ckt 1,2 | 64 | 0 | 64 | 13 | 4 | 7: 14; 8: 15; 5+6 P1 9: 1; 5+6 P2 10: 11; 5+6 P3 11: 0.75733; 5+6 P4 12: O/C E/f R-Phase | [12 empty] | 65 | 16.00-16.15 | 50.11 |  | 1208
2 | [33 empty] | 66 | 16.15-16.30 | 50.01 |  | 1187 | bar: 5+6 P12 21
3 | [33 empty] | 67 | 16.30-16.45 | 49.99 |  | 1185 | bar: 5+6 P12 21
4 | [33 empty] | 68 | 16.45-17.00 | 49.98 | 50.0225 | 1164 | 1186 | bar: 5+6 P12 21
5 | [33 empty] | 69 | 17.00-17.15 | 49.99 |  | 1181 | bar: 5+6 P12 21
6 | [33 empty] | 70 | 17.15-17.30 | 49.98 |  | 1180 | bar: 5+6 P12 21
7 | [33 empty] | 71 | 17.30-17.45 | 49.95 |  | 1163 | bar: 5+6 P12 21
8 | [33 empty] | 72 | 17.45-18.00 | 49.97 | 49.9725 | 1157 | 1170.25 | bar: 5+6 P12 21
[34 empty] | 73 | 18.00-18.15 | 49.97 |  | 1156 | bar: 5+6 P12 21
[34 empty] | 74 | 18.15-18.30 | 49.9 |  | 1162 | bar: 5+6 P12 21
[34 empty] | 75 | 18.30-18.45 | 49.99 |  | 1166 | bar: 5+6 P12 21
[34 empty] | 76 | 18.45-19.00 | 49.96 | 49.955 | 1190 | 1168.5 | bar: 5+6 P12 21
[34 empty] | 77 | 19.00-19.15 | 49.94 |  | 1219 | bar: 5+6 P12 21
[34 empty] | 78 | 19.15-19.30 | 49.95 |  | 1293 | bar: 5+6 P12 21
[34 empty] | 79 | 19.30-19.45 | 50 |  | 1316 | bar: 5+6 P12 21
[34 empty] | 80 | 19.45-20.00 | 50.03 | 49.98 | 1315 | 1285.75 | bar: 5+6 P12 21
[34 empty] | 81 | 20.00-20.15 | 50.02 |  | 1288 | bar: 5+6 P12 21
[34 empty] | 82 | 20.15-20.30 | 49.97 |  | 1272 | bar: 5+6 P12 21
[34 empty] | 83 | 20.30-20.45 | 49.93 |  | 1255 | bar: 5+6 P12 21
[34 empty] | 84 | 20.45-21.00 | 49.96 | 49.97 | 1235 | 1262.5 | bar: 5+6 P12 21
[34 empty] | 85 | 21.00-21.15 | 49.95 |  | 1206 | bar: 5+6 P12 21
[34 empty] | 86 | 21.15-21.30 | 49.96 |  | 1168 | bar: 5+6 P12 21
[34 empty] | 87 | 21.30-21.45 | 50.02 |  | 1156
[34 empty] | 88 | 21.45-22.00 | 50.03 | 49.99 | 1134 | 1166
[34 empty] | 89 | 22.00-22.15 | 50.04 |  | 1104
[34 empty] | 90 | 22.15-22.30 | 50.01 |  | 1087
[34 empty] | 91 | 22.30-22.45 | 50 |  | 1074
[34 empty] | 92 | 22.45-23.00 | 50 | 50.0125 | 1056 | 1080.25
[34 empty] | 93 | 23.00-23.15 | 50 |  | 1030
[34 empty] | 94 | 23.15-23.30 | 49.98 |  | 1027
[34 empty] | 95 | 23.30-23.45 | 50.02 |  | 1008
[34 empty] | 96 | 23.45-24.00 | 50.04 | 50.01 | 1002 | 1016.75
[35 empty] | Total | 49.9871 | 49.9871 | 29384 | 29384
[35 empty] | max | 1501 |  | avg. max | 1491.75
[35 empty] | min | 1002 |  | avg. min | 1016.75
Note on AG16: ReportServer: critical formulas…….do not disturb
Note on AH16: ReportServer: critical formulas…….do not disturb
Note on Y24: Please don't edit here
Note on H25: Column no. 5 =Sum (2+3+4 Column)
Note on L25: The fig of power cut comes from daily hourly load sheet.