## Form-15_DTR
MULTIPLE ELEMENT TRIPPING REPORT OF LINES SUMMARY
HIMACHAL PRADESH
STATE LOAD DESPATCH CENTER
Monthly Multiple Element Tripping Report Summary For The Month Of March 2024
Sr. No. | Date | Name of Transmission Line | Tripping Time |  | Restoration Time |  | Duration |  | Generation Loss | Reason of Tripping | Tripping due to the Element
|  |  | Hour | Minute | Hour | Minute | Hour | Minute | (MW)
1 | 03-Mar-2024 | 400 KV Kala Amb(PKTL)-Wangto_GIS(HP) (HPPTCL) Ckt-1 | 2 | 22 | 5 | 39 | 3 | 17 | 0 | Wangtoo Kala Amb Ckt tripped at 02:22 Hours and fault was cleared by Distance Protection Main 1 & Main 2. Probable cause shared by PHTL team was heavy rain fall in the area. 3. Fault Current Iy = 7.631 kA Ib = 7.652 kA
2 | 03-Mar-2024 | 400 KV Wangto_GIS(HP)-Sorang(Greenko) (Greenko) Ckt-1 | 4 | 45 | 6 | 51 | 2 | 6 | 0 | 1.Wangtoo Sorang Ckt tripped at 04:45 Hours and fault was cleared by Distance Protection Main 1 & Main 2.Probable cause shared by PHTL team was heavy rain fall in the area. 3.Fault Current Ib = 6.3 kA In = 6.4 kA
3 | 03-Mar-2024 | 400 KV Kala Amb(PKTL)-Wangto_GIS(HP) (HPPTCL) Ckt-1 | 5 | 45 | 11 | 5 | 6 | 40 | 0 | Wangtoo Kala Amb Ckt tripped at 05:45 Hours and fault was cleared by distance protection main 2. Probable cause shared by PHTL team was heavy rain fall in the area. Fault Current Ib = 1.145 kA In = 1.152 Ka
4 | 2024-03-11 | 220 KV Charor(HP)-Parbati Pooling Banala(PG) (HPPTCL) Ckt-2 | 16 | 19 | 19 | 39 | 3 | 20 | 0 | CB opened at Banala Substation
5 | 2024-03-11 | 220 KV Charor(HP)-Parbati Pooling Banala(PG) (HPPTCL) Ckt-1 | 16 | 19 | 19 | 33 | 3 | 14 | 0 | CB opened at Banala Substation
6 | 2024-03-30 | 132 KV Dehar(BB)-Kangoo(HP) (HPPTCL) Ckt-1 | 4 | 9 | 5 | 54 | 1 | 45 | 49 | SF-6 Breaker tripped off at Dehar Power House. Due to Bad wheather conditins & Heavy Lightning
7 | 2024-03-30 | 220 KV Hamirpur(PG)-Dehan (HP) (HPPTCL) Ckt-1 | 4 | 18 | 17 | 28 | 13 | 10 | 0 | R phase Zone 1 Fault current: I(R)-354 A, I(N)-592A Maintenance team done the patrolling of 220 kV D/C Dehan Hamirpur transmission line . No visible issue/discrepancy has been found.
8 | 2024-03-30 | 220 KV Dehar(BB)-Kangoo(HP) (HP) Ckt-1 | 4 | 24 | 5 | 54 | 1 | 30 | 49 | SF- 6 Breaker tripped off at Dehar power house. Due to bad wheather condition & Heavy lightning
9 | 2024-03-30 | 132 KV Hamirpur(HP)-Chohal (PS) (PSTCL) Ckt-1 | 5 | 10 | 19 | 43 | 14 | 33 | 0 | 132 kv Anu – Chauhal ckt tripped off at 04:55 hrs dated 30/03/2024 due to heavy rain and bad weather Ib = 2.632 KA In = 2.782 KA
10 | 2024-03-31 | 220 KV Bairasiul(NH)-Jessore(HP) (PG) Ckt-1 | 0 | 1 | 9 | 25 | 9 | 24 | 0 | Due to Over voltage at Bairasuil end.
11 | 2024-03-31 | 132 KV Dehar(BB)-Kangoo(HP) (HPPTCL) Ckt-1 | 0 | 35 | 1 | 45 | 1 | 10 | 0 | SF-6 Breaker Tripped off at Dehar Power house
Total:- | [8 empty] | 98