## Report_PSPR NRLDC SLDC
File Name: PSPR- |  |  | 2024-04-16
Hiamchal Pradesh State Load Despatch Centre
[18 empty] | DATED | 2024-04-17
FROM | [15 empty] | TO
| POWER CONTROLLER | [16 empty] | D.G.M.,NRLDC,NEW DELHI
| HPSLDC, GoHP, Totu, Shimla-11 | [16 empty] | FAX # 011-26852747-26853082
(FAX #: 0177 2837543)
|  |  | DEMAND AND POWER SUPPLY POSITION | [18 empty] | DEMAND OF STATE |  |  | 29525.25 | MWh
[22 empty] | ACTUAL MALANA GENERATION |  |  | 716 | MWh
|  | State:- Himachal Pradesh | [19 empty] | ACTUAL BASPA GENERATION |  |  | 1292.2 | MWh | MALANA-II | 639 | MWh |  |  |  |  | SN | Time Block | Frequency | Avg. Freq. | Demand | Avg Demand
[18 empty] | PEAK DEMAND(MW) |  | 1535.9096 | [6 empty] | HOLI BAJOLI | 3010 | MWh |  |  |  |  | 1 | 00.00-00.15 | 49.92 |  | 876
|  | Month/Day :- |  |  |  |  | 2024-04-16 | [10 empty] | Min.DEMAND(MW) |  | 828 |  | ACTUAL OWN GENERATION |  |  | 12478.173 | MWh | SWARA KUDDU | 603.354 | MWh |  |  |  |  | 2 | 00.15-00.30 | 49.95 |  | 857
[34 empty] | 3 | 00.30-00.45 | 50.01 |  | 850 |  | for VLOOKUP(MaxGenHrs.)
HRS. OF THE DAY | GENERATION (MW) | [6 empty] | NET IMPORT (MW) | DEMAND MET (MW) | FREQ-UENCY CORREC-TION (MW) | DEMAND NOT MET | [7 empty] | TOTAL DEMAND NOT MET (MW) | TOTAL ENERGY EQUIVA-LENT TO DEMAND NOT MET (MU) | TOTAL UNRESTRI-CTED DEMAND (MW) P7=P1+P2+P11 | HRS. OF THE DAY | GENERATION (MW) |  |  |  | AVERAGE DEMAND MET (MW) | MAX DEMAND (HOURLY) | MIN DEMAND (HOURLY) | DEMAND ADJUSTMENT(MAXIMUM/MINIMUM/AVERAGE) | CALCULATION MAX/MIN ACTUAL | DEMAND TREND | DUE TO LOAD SHEDD-ING (MW) | 4 | 00.45-01.00 | 50.02 | 49.975 | 857 | 860 | Malana | HRS. OF THE DAY | TIME | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | TOTAL
[11 empty] | Low Availability (in MW) | Financial Constraints (in MW) | Emergency load shedding due to security and reliability of the Grid-over Drawl (in MW) | Planned maintenance in transmission system (in MW) | Distribution constraints (in MW) | Planned maintenance in distribution system (in MW) | Tranmission constraints | Any other reasion ( to be specfied) (MW) | [15 empty] | 5 | 01.00-01.15 | 49.99 |  | 853 |  |  |  | MALANA-2 | 28 | 28 | 28 | 21.5 | 29.5 | 99.25 | 99.75 | 99.25 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 25.75 | 28 | 28 | 28 | 28 | 28 | 28 | 629
[34 empty] | 6 | 01.15-01.30 | 50.02 |  | 841 |  |  |  | SWARA KUDDU | 0 | 0 | 0 | 0 | 10 | 37 | 70.75 | 70.5 | 37 | 37 | 18.75 | 0 | 0 | 0 | 0 | 0 | 0 | 9.75 | 37 | 37 | 37 | 37.5 | 81 | 81 | 601.25
[34 empty] | 7 | 01.30-01.45 | 50.01 |  | 831
[34 empty] | 8 | 01.45-02:00 | 50.02 | 50.01 | 834 | 839.75
| OWN GEN | Malana | BASPA | MALANA-II | SAWRA KUDDU | BAJOLI HOLI | TOTAL | [15 empty] | OWN Generation | Malana | BASPA | TOTAL | [7 empty] | 9 | 02.00-02.15 | 50 |  | 848 |  | Malana
[9 empty] | 5+6 | [24 empty] | 10 | 02.15-02.30 | 50.01 |  | 830
[9 empty] | P1 | P2 | P3 | P4 | P5 | P6 | P7 | P8 | P9 | P10 | P11 | P11/1000 | P12 | [5 empty] | P1 | [5 empty] | P3 | 11 | 02.30-02.45 | 50 |  | 828
1 | 2 | 3 | 4 | 5 | 6 |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 7 | 8 | 9 | 10 | 12 | 02.45-03:00 | 50.02 | 50.0075 | 828 | 833.5
1 | 590.8556 | 44.5181 | 86.5464 | 28 | 0 | 105.75 | 855.6701 | 3.995 | 859.6652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 859.6652 | 1 | 605.3333 | 45 | 83 | 733.3333 | 860 | 876 | 850 | 860 | 860 | 859.6652 | 0 | 13 | 03.00-03.15 | 49.97 |  | 834 |  | 45 | 1
2 | 524.97 | 34.8725 | 47.9655 | 28 | 0 | 165 | 800.808 | 38.615 | 839.423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 839.423 | 2 | 537.8333 | 35.25 | 46 | 619.0833 | 839.75 | 853 | 831 | 839.75 | 839.75 | 839.423 | 0 | 14 | 03.15-03.30 | 50 |  | 843 |  | 35.25 | 2
3 | 533.3887 | 34.6252 | 50.3116 | 28 | 0 | 190 | 836.3256 | -8.3256 | 828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 828 | 3 | 546.4583 | 35 | 48.25 | 629.7083 | 833.5 | 848 | 828 | 828 | 828 | 828 | 0 | 15 | 03.30-03.45 | 49.98 |  | 854 |  | 35 | 3
4 | 500.5679 | 39.3244 | 1.3034 | 21.5 | 0 | 186 | 748.6957 | 97.4747 | 846.1704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 846.1704 | 4 | 512.8333 | 39.75 | 1.25 | 553.8333 | 846.5 | 855 | 834 | 846.5 | 846.5 | 846.1704 | 0 | 16 | 03.45-04.00 | 50.01 | 49.99 | 855 | 846.5 | 39.75 | 4
5 | 464.4285 | 43.5288 | 0 | 29.5 | 10 | 186 | 733.4573 | 159.9447 | 893.402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 893.402 | 5 | 475.8083 | 44 | 0 | 519.8083 | 893.75 | 934 | 857 | 893.75 | 893.75 | 893.402 | 0 | 17 | 04.00-04.15 | 49.98 |  | 857 |  | 44 | 5
6 | 591.3925 | 44.0235 | 55.2646 | 99.25 | 37 | 160.75 | 987.6805 | 88.6503 | 1076.3308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1076.3308 | 6 | 605.8833 | 44.5 | 53 | 703.3833 | 1076.75 | 1224 | 965 | 1076.75 | 1076.75 | 1076.3308 | 0 | 18 | 04.15-04.30 | 49.96 |  | 872 |  | 44.5 | 6
7 | 613.5984 | 44.5181 | 206.7207 | 99.75 | 70.75 | 133.25 | 1168.5872 | 248.6108 | 1417.198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 2.4 | 0.0024 | 1419.598 | 7 | 628.6333 | 45 | 198.25 | 871.8833 | 1417.75 | 1492 | 1320 | 1417.75 | 1417.75 | 1417.198 | 2.4 | 19 | 04.30-04.45 | 49.97 |  | 912 |  | 45 | 7
8 | 500.5435 | 44.5181 | 51.615 | 99.25 | 70.5 | 103 | 869.4267 | 646.4829 | 1515.9096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 20 | 0.02 | 1535.9096 | 8 | 512.8083 | 45 | 49.5 | 607.3083 | 1516.5 | 1525 | 1505 | 1516.5 | 1516.5 | 1515.9096 | 20 | 20 | 04.45-05.00 | 49.97 | 49.97 | 934 | 893.75 | 45 | 8
9 | 513.0618 | 34.8725 | 0 | 1.75 | 37 | 101.25 | 687.9343 | 840.0657 | 1528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1528 | 9 | 525.6333 | 35.25 | 0 | 560.8833 | 1511 | 1528 | 1492 | 1528 | 1528 | 1528 | 0 | 21 | 05.00-05.15 | 49.96 |  | 965 |  | 35.25 | 9
10 | 503.2522 | 34.6252 | 0 | 0 | 37 | 101.5 | 676.3774 | 799.2978 | 1475.6752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1475.6752 | 10 | 515.5833 | 35 | 0 | 550.5833 | 1476.25 | 1494 | 1464 | 1476.25 | 1476.25 | 1475.6752 | 0 | 22 | 05.15-05.30 | 49.95 |  | 1016 |  | 35 | 10
11 | 480.5582 | 9.1509 | 0 | 0 | 18.75 | 97.75 | 606.2092 | 838.4781 | 1444.6873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1444.6873 | 11 | 492.3333 | 9.25 | 0 | 501.5833 | 1445.25 | 1450 | 1441 | 1445.25 | 1445.25 | 1444.6873 | 0 | 23 | 05.30-05.45 | 49.98 |  | 1102 |  | 9.25 | 11
12 | 521.7978 | 0 | 0 | 0 | 0 | 101 | 622.7978 | 798.3987 | 1421.1964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1421.1964 | 12 | 534.5833 | 0 | 0 | 534.5833 | 1421.75 | 1429 | 1416 | 1421.75 | 1421.75 | 1421.1964 | 0 | 24 | 05.45-06.00 | 50 | 49.9725 | 1224 | 1076.75 | 0 | 12
13 | 500.3239 | 0 | 0 | 0 | 0 | 102.5 | 602.8239 | 762.1444 | 1364.9683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1364.9683 | 13 | 512.5833 | 0 | 0 | 512.5833 | 1365.5 | 1385 | 1306 | 1365.5 | 1365.5 | 1364.9683 | 0 | 25 | 06.00-06.15 | 50.04 |  | 1320 |  | 0 | 13
14 | 440.9293 | 0.24732 | 0 | 0 | 0 | 103 | 544.1766 | 756.3169 | 1300.4935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1300.4935 | 14 | 451.7333 | 0.25 | 0 | 451.9833 | 1301 | 1317 | 1297 | 1301 | 1301 | 1300.4935 | 0 | 26 | 06.15-06.30 | 50.03 |  | 1404 |  | 0.25 | 14
15 | 525.1408 | 10.8822 | 0 | 0 | 0 | 102 | 638.023 | 677.7145 | 1315.7375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1315.7375 | 15 | 538.0083 | 11 | 0 | 549.0083 | 1316.25 | 1326 | 1309 | 1316.25 | 1316.25 | 1315.7375 | 0 | 27 | 06.30-06.45 | 50.05 |  | 1455 |  | 11 | 15
16 | 540.1725 | 10.8822 | 0 | 0 | 0 | 114 | 665.0547 | 681.1709 | 1346.2256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1346.2256 | 16 | 553.4083 | 11 | 0 | 564.4083 | 1346.75 | 1368 | 1302 | 1346.75 | 1346.75 | 1346.2256 | 0 | 28 | 06.45-07.00 | 50.06 | 50.045 | 1492 | 1417.75 | 11 | 16
17 | 558.7425 | 10.8822 | 27.3716 | 0.25 | 0 | 125 | 722.2463 | 623.2296 | 1345.4759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1345.4759 | 17 | 572.4333 | 11 | 26.25 | 609.6833 | 1346 | 1361 | 1320 | 1346 | 1346 | 1345.4759 | 0 | 29 | 07.00-07.15 | 50.07 |  | 1505 |  | 11 | 17
18 | 538.7328 | 26.9582 | 80.8114 | 25.75 | 9.75 | 131.5 | 813.5024 | 498.7365 | 1312.2389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1312.2389 | 18 | 551.9333 | 27.25 | 77.5 | 656.6833 | 1312.75 | 1317 | 1306 | 1312.75 | 1312.75 | 1312.2389 | 0 | 30 | 07.15-07.30 | 50.11 |  | 1525 |  | 27.25 | 18
19 | 495.2971 | 43.5288 | 96.1916 | 28 | 37 | 136 | 836.0175 | 444.4837 | 1280.5012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1280.5012 | 19 | 507.4333 | 44 | 92.25 | 643.6833 | 1281 | 1298 | 1265 | 1281 | 1281 | 1280.5012 | 0 | 31 | 07.30-07.45 | 50.03 |  | 1518 |  | 44 | 19
20 | 490.4167 | 43.5288 | 143.375 | 28 | 37 | 136 | 878.3205 | 470.1542 | 1348.4748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1348.4748 | 20 | 502.4333 | 44 | 137.5 | 683.9333 | 1349 | 1363 | 1315 | 1349 | 1349 | 1348.4748 | 0 | 32 | 07.45-08.00 | 50.04 | 50.0625 | 1518 | 1516.5 | 44 | 20
21 | 500.1775 | 29.9261 | 141.2896 | 28 | 37 | 120.75 | 857.1432 | 447.0988 | 1304.242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1304.242 | 21 | 512.4333 | 30.25 | 135.5 | 678.1833 | 1304.75 | 1319 | 1289 | 1304.75 | 1304.75 | 1304.242 | 0 | 33 | 08.00-08.15 | 50 |  | 1528 |  | 30.25 | 21
22 | 519.4552 | 43.5288 | 181.6953 | 28 | 37.5 | 120 | 930.1793 | 314.0861 | 1244.2654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1244.2654 | 22 | 532.1833 | 44 | 174.25 | 750.4333 | 1244.75 | 1278 | 1200 | 1244.75 | 1244.75 | 1244.2654 | 0 | 34 | 08.15-08.30 | 49.98 |  | 1519 |  | 44 | 22
23 | 504.5699 | 43.5288 | 90.4566 | 28 | 81 | 112.5 | 860.0553 | 288.9971 | 1149.0524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1149.0524 | 23 | 516.9333 | 44 | 86.75 | 647.6833 | 1149.5 | 1168 | 1126 | 1149.5 | 1149.5 | 1149.0524 | 0 | 35 | 08.30-08.45 | 49.97 |  | 1505 |  | 44 | 23
24 | 525.7997 | 43.5288 | 31.2818 | 28 | 81 | 105 | 814.6104 | 254.2233 | 1068.8337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1068.8337 | 24 | 538.6833 | 44 | 30 | 612.6833 | 1069.25 | 1095 | 1050 | 1069.25 | 1069.25 | 1068.8337 | 0 | 36 | 08.45-09.00 | 50.02 | 49.9925 | 1492 | 1511 | 44 | 24
[34 empty] | 37 | 09.00-09.15 | 50.03 |  | 1494
TOTAL (in MWh) | 12478.173 | 716 | 1292.2 | 629 | 601.25 | 3039.5 | 18756.123 | 10770.0443 | 29526.1673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.4 | 0 | 22.4 | 0.0224 | 29548.5673 | TOTAL | 12783.925 | 723.75 | 1239.25 | 14746.925 | 29525.25 |  |  | 29536.75 | 29536.75 | 29526.1673 | 22.4 | 38 | 09.15-09.30 | 50.01 |  | 1471
[34 empty] | 39 | 09.30-09.45 | 50.03 |  | 1476
[34 empty] | 40 | 09.45-10.00 | 50.03 | 50.025 | 1464 | 1476.25
|  |  | Hourly Average Frequency (Fr) |  |  |  | 5+6 P4 12: 50.0104; 5+6 P6 14: HZ | Note :- Please don't edit these figures. | [11 empty] | 41 | 10.00-10.15 | 50.04 |  | 1441
|  |  | Demand met for the day |  |  |  | 5+6 P4 12: 1528; 5+6 P6 14: MW | [12 empty] | 42 | 10.15-10.30 | 50.03 |  | 1441
|  |  | Unrestricted Demand for the day |  |  |  | 5+6 P4 12: 1535.9096; 5+6 P6 14: MW | MAX = | 1528 | [10 empty] | 43 | 10.30-10.45 | 50.02 |  | 1450
|  |  | Minimum Demand(Unrestricted) for the day |  |  |  | 5+6 P4 12: 828; 5+6 P6 14: MW; 5+6 P11 19: Aux.; 5+6 P11/1000 20: Net gen. | MIN = | 828 | [10 empty] | 44 | 10.45-11.00 | 49.99 | 50.02 | 1449 | 1445.25
|  |  | Gross own generation |  |  |  | 5+6 P4 12: 12478.173; 5+6 P6 14: MWH; 5+6 P11 19: 26.7052; 5+6 P11/1000 20: 12451.4678 | [12 empty] | 45 | 11.00-11.15 | 49.99 |  | 1425
|  |  | Gross Baspa generation |  |  |  | 5+6 P4 12: 1292.2; 5+6 P6 14: MWH; 5+6 P11 19: 21.1; 5+6 P11/1000 20: 1271.1 | [12 empty] | 46 | 11.15-11.30 | 50.02 |  | 1429
|  |  | Gross Malana generation |  |  |  | 5+6 P4 12: 716; 5+6 P6 14: MWH; 5+6 P11 19: 1.848; 5+6 P11/1000 20: 714.152 | [12 empty] | 47 | 11.30-11.45 | 50 |  | 1417
|  |  | Malana generation at 0300 Hrs. |  |  |  | 5+6 P4 12: 35; 5+6 P6 14: MW | [12 empty] | 48 | 11.45-12.00 | 49.98 | 49.9975 | 1416 | 1421.75
|  |  | Malana generation at 2400 Hrs. |  |  |  | 5+6 P4 12: 44; 5+6 P6 14: MW | [12 empty] | 49 | 12.00-12.15 | 49.97 |  | 1385
|  |  | Max.generation of Malana at 100 Hrs. |  |  |  | 5+6 P4 12: 45; 5+6 P6 14: MW | [12 empty] | 50 | 12.15-12.30 | 50 |  | 1363
[7 empty] | 5+6 P2 10: Off Peak Hrs MW; 5+6 P4 12: Peak Hrs MW; 5+6 P11 19: Gross Lus; 5+6 P11/1000 20: Net Lus | [14 empty] | 50.03 |  | 1368
|  |  | Total Own Generation |  |  |  | 5+6 P2 10: 539.4346; 5+6 P4 12: 445.5491; 5+6 P11 19: 124.7817; 5+6 P11/1000 20: 124.5147 | [12 empty] | 51 | 12.30-12.45 | 50.01 | 50.0025 | 1346 | 1365.5
|  |  | Above 25 MW |  |  |  | 5+6 P2 10: 150.2142; 5+6 P4 12: 101.7662; 5+6 P11 19: 30.6401; 5+6 P11/1000 20: 30.418 | [12 empty] | 52 | 12.45-13.00 | 50.1 |  | 1306
|  |  | Below 25 MW(Small Hydro <25 MW) |  |  |  | 5+6 P2 10: 389.2205; 5+6 P4 12: 343.7828; 5+6 P11 19: 94.1416; 5+6 P11/1000 20: 94.0967 | [12 empty] | 53 | 13.00-13.15 | 50.04 |  | 1284
[34 empty] | 55 | 13.30-13.45 | 50 |  | 1297
[34 empty] | 56 | 13.45-14.00 | 50.02 | 50.04 | 1317 | 1301
[7 empty] | 5+6 P11 19: Shift Incharge | [12 empty] | 57 | 14.00-14.15 | 49.98 |  | 1312
[7 empty] | 5+6 P11 19: HPSLDC, GoHP, Totu,Shimla-11. | [12 empty] | 58 | 14.15-14.30 | 49.99 |  | 1309
Load Shedding For Dated | [6 empty] | 5+6 P1 9: 2024-04-16 | [12 empty] | 59 | 14.30-14.45 | 49.98 |  | 1326
[34 empty] | 60 | 14.45-15.00 | 49.98 | 49.9825 | 1318 | 1316.25 | bar: 7 to 5+6 P4 12; 5+6 P12 21
SR.NO. | NAME OF FEEDER / SubStation | LOAD IN MW |  |  | TIME PERIOD |  | 5+6 P1 9: DURATION; 5+6 P3 11: LOAD SHEDDING IN LUS; 5+6 P4 12: REASON | [12 empty] | 61 | 15.00-15.15 | 50 |  | 1302
|  | BEFORE SHEDD-ING | AFTER SHEDD-ING | LOAD SHEDD-ING | FROM | [28 empty] | 62 | 15.15-15.30 | 50.01 |  | 1355 | bar: 7 to 5+6 P4 12; 5+6 P12 21
[5 empty] | Hour | Minute | 7: Hour; 8: Minute; 5+6 P1 9: Hour; 5+6 P2 10: Minute | [12 empty] | 63 | 15.30-15.45 | 50.02 |  | 1368
1 | 2 | 3 | 4 | 5 | 6 | 7 | 7: 8; 8: 9; 5+6 P1 9: 10; 5+6 P2 10: 11; 5+6 P3 11: 12; 5+6 P4 12: 13 | [12 empty] | 64 | 15.45-16.00 | 50.01 | 50.01 | 1362 | 1346.75
1 | 132 kV Una-Amb line | 24 | 0 | 24 | 6 | 54 | 7: 7; 8: 50; 5+6 P1 9: 0; 5+6 P2 10: 56; 5+6 P3 11: 0.224; 5+6 P4 12: C.B tripped due to internal fault in 132 kV SF-6 circuit breaker | [12 empty] | 65 | 16.00-16.15 | 50.07 |  | 1361
2 | [33 empty] | 66 | 16.15-16.30 | 50.02 |  | 1344 | bar: 5+6 P12 21
3 | [33 empty] | 67 | 16.30-16.45 | 50.02 |  | 1359 | bar: 5+6 P12 21
4 | [33 empty] | 68 | 16.45-17.00 | 50.01 | 50.03 | 1320 | 1346 | bar: 5+6 P12 21
5 | [33 empty] | 69 | 17.00-17.15 | 50.03 |  | 1317 | bar: 5+6 P12 21
6 | [33 empty] | 70 | 17.15-17.30 | 49.99 |  | 1311 | bar: 5+6 P12 21
7 | [33 empty] | 71 | 17.30-17.45 | 50.01 |  | 1317 | bar: 5+6 P12 21
8 | [33 empty] | 72 | 17.45-18.00 | 49.95 | 49.995 | 1306 | 1312.75 | bar: 5+6 P12 21
[34 empty] | 73 | 18.00-18.15 | 50.04 |  | 1298 | bar: 5+6 P12 21
[34 empty] | 74 | 18.15-18.30 | 50.02 |  | 1290 | bar: 5+6 P12 21
[34 empty] | 75 | 18.30-18.45 | 49.98 |  | 1271 | bar: 5+6 P12 21
[34 empty] | 76 | 18.45-19.00 | 50.01 | 50.0125 | 1265 | 1281 | bar: 5+6 P12 21
[34 empty] | 77 | 19.00-19.15 | 50.01 |  | 1315 | bar: 5+6 P12 21
[34 empty] | 78 | 19.15-19.30 | 50.01 |  | 1359 | bar: 5+6 P12 21
[34 empty] | 79 | 19.30-19.45 | 50.03 |  | 1359 | bar: 5+6 P12 21
[34 empty] | 80 | 19.45-20.00 | 50.05 | 50.025 | 1363 | 1349 | bar: 5+6 P12 21
[34 empty] | 81 | 20.00-20.15 | 50.06 |  | 1319 | bar: 5+6 P12 21
[34 empty] | 82 | 20.15-20.30 | 50.04 |  | 1311 | bar: 5+6 P12 21
[34 empty] | 83 | 20.30-20.45 | 50.01 |  | 1300 | bar: 5+6 P12 21
[34 empty] | 84 | 20.45-21.00 | 50.04 | 50.0375 | 1289 | 1304.75 | bar: 5+6 P12 21
[34 empty] | 85 | 21.00-21.15 | 50.01 |  | 1278 | bar: 5+6 P12 21
[34 empty] | 86 | 21.15-21.30 | 50.01 |  | 1272 | bar: 5+6 P12 21
[34 empty] | 87 | 21.30-21.45 | 50.02 |  | 1229
[34 empty] | 88 | 21.45-22.00 | 50.05 | 50.0225 | 1200 | 1244.75
[34 empty] | 89 | 22.00-22.15 | 50.02 |  | 1167
[34 empty] | 90 | 22.15-22.30 | 50 |  | 1168
[34 empty] | 91 | 22.30-22.45 | 50 |  | 1137
[34 empty] | 92 | 22.45-23.00 | 50 | 50.005 | 1126 | 1149.5
[34 empty] | 93 | 23.00-23.15 | 50 |  | 1095
[34 empty] | 94 | 23.15-23.30 | 50.03 |  | 1072
[34 empty] | 95 | 23.30-23.45 | 50.01 |  | 1050
[34 empty] | 96 | 23.45-24.00 | 50.04 | 50.02 | 1060 | 1069.25
[35 empty] | Total | 50.0104 | 50.0104 | 29525.25 | 29525.25
[35 empty] | max | 1528 |  | avg. max | 1516.5
[35 empty] | min | 828 |  | avg. min | 833.5
Note on AG16: ReportServer: critical formulas…….do not disturb
Note on AH16: ReportServer: critical formulas…….do not disturb
Note on Y24: Please don't edit here
Note on H25: Column no. 5 =Sum (2+3+4 Column)
Note on L25: The fig of power cut comes from daily hourly load sheet.